## Tổng quát
Modbus Register | Number register | Adr | Size | Description | Range | Default | Format | Property | Comment
0 | 2 | 0 | 4 | device info |  | STC1 | string | Read | Sensor tag receiver
2 | 4 | 4 | 8 | firmware version |  | 1.6 | string | Read
6 | 2 | 12 | 4 | hardware version |  | 2 | string | Read
8 | 20 | 16 | 40 | rssi node 1..40 |  |  | int8 | Read
28 | 20 | 56 | 40 | data status node 1..40 | 0-9 99 |  | uint8 | Read | n = thời gian từ lúc nhận được data mới nhất của sensor đến hiện tại data status = 99: khi chưa nhận được bất kỳ data nào 0: khi n <= cmp time 1 1: khi cmp time 1 < n <= cmp time 2 2: khi cmp time 2 < n <= cmp time 3 3: khi cmp time 3 < n <= cmp time 4 4: khi cmp time 4 < n <= cmp time 5 5: khi cmp time 5 < n <= cmp time 6 6: khi cmp time 6 < n <= cmp time 7 7: khi cmp time 7 < n <= cmp time 8 8: khi cmp time 8 < n <= cmp time 9 9: khi cmp time n > cmp time 9
48 | 20 | 96 | 40 | rf timeout count node 1..40 | 0-255 |  | uint8 | Read | đếm khi data status >=3
68 | 20 | 136 | 40 | rssi status node 1..40 | 0-4 |  | uint8 | Read | + RSSI = 0..-54dBm => RSSI Status = 4 (sóng RF mạnh nhất) + RSSI = -55..-69dBm => RSSI Status = 3 + RSSI = -70..-79dBm => RSSI Status = 2 + RSSI = -80..-100dBm => RSSI Status = 1 + RSSI < -100dBm => RSSI Status = 0
88 | 60 | 176 | 120 | spare |  |  | uint8 | Read
148 | 20 | 296 | 40 | rx seq node 1..40 | 0-255 |  | uint8 | Read
168 | 20 | 336 | 40 | rx duplication count node 1..40 | 0-255 |  | uint8 | Read
188 | 20 | 376 | 40 | sync status node 1..40 | 0-2, 99 |  | uint8 | Read | 0: sync ok, 1: sync start, 2: cfg error, 99: nothing to sync
41216 | 32 |  | 64 | Data area of Node 1 |  |  |  | Read | 0xA100..0xA120
41472 | 32 |  | 64 | Data area of Node 2 |  |  |  | Read | 0xA200..0xA220
41728 | 32 |  | 64 | Data area of Node 3 |  |  |  | Read | 0xA300..0xA320
41984 | 32 |  | 64 | Data area of Node 4 |  |  |  | Read | 0xA400..0xA420
42240 | 32 |  | 64 | Data area of Node 5 |  |  |  | Read | 0xA500..0xA520
42496 | 32 |  | 64 | Data area of Node 6 |  |  |  | Read | 0xA600..0xA620
42752 | 32 |  | 64 | Data area of Node 7 |  |  |  | Read | 0xA700..0xA720
43008 | 32 |  | 64 | Data area of Node 8 |  |  |  | Read | 0xA800..0xA820
43264 | 32 |  | 64 | Data area of Node 9 |  |  |  | Read | 0xA900..0xA920
43520 | 32 |  | 64 | Data area of Node 10 |  |  |  | Read | 0xAA00..0xAA20
45312 | 32 |  | 64 | Data area of Node 11 |  |  |  | Read | 0xB100..0xB120
45568 | 32 |  | 64 | Data area of Node 12 |  |  |  | Read | 0xB200..0xB220
45824 | 32 |  | 64 | Data area of Node 13 |  |  |  | Read | 0xB300..0xB320
46080 | 32 |  | 64 | Data area of Node 14 |  |  |  | Read | 0xB400..0xB420
46336 | 32 |  | 64 | Data area of Node 15 |  |  |  | Read | 0xB500..0xB520
46592 | 32 |  | 64 | Data area of Node 16 |  |  |  | Read | 0xB600..0xB620
46848 | 32 |  | 64 | Data area of Node 17 |  |  |  | Read | 0xB700..0xB720
47104 | 32 |  | 64 | Data area of Node 18 |  |  |  | Read | 0xB800..0xB820
47360 | 32 |  | 64 | Data area of Node 19 |  |  |  | Read | 0xB900..0xB920
47616 | 32 |  | 64 | Data area of Node 20 |  |  |  | Read | 0xBA00..0xBA20
49408 | 32 |  | 64 | Data area of Node 21 |  |  |  | Read | 0xC100..0xC120
49664 | 32 |  | 64 | Data area of Node 22 |  |  |  | Read | 0xC200..0xC220
49920 | 32 |  | 64 | Data area of Node 23 |  |  |  | Read | 0xC300..0xC320
50176 | 32 |  | 64 | Data area of Node 24 |  |  |  | Read | 0xC400..0xC420
50432 | 32 |  | 64 | Data area of Node 25 |  |  |  | Read | 0xC500..0xC520
50688 | 32 |  | 64 | Data area of Node 26 |  |  |  | Read | 0xC600..0xC620
50944 | 32 |  | 64 | Data area of Node 27 |  |  |  | Read | 0xC700..0xC720
51200 | 32 |  | 64 | Data area of Node 28 |  |  |  | Read | 0xC800..0xC820
51456 | 32 |  | 64 | Data area of Node 29 |  |  |  | Read | 0xC900..0xC920
51712 | 32 |  | 64 | Data area of Node 30 |  |  |  | Read | 0xCA00..0xCA20
53504 | 32 |  | 64 | Data area of Node 31 |  |  |  | Read | 0xD100..0xD120
53760 | 32 |  | 64 | Data area of Node 32 |  |  |  | Read | 0xD200..0xD220
54016 | 32 |  | 64 | Data area of Node 33 |  |  |  | Read | 0xD300..0xD320
54272 | 32 |  | 64 | Data area of Node 34 |  |  |  | Read | 0xD400..0xD420
54528 | 32 |  | 64 | Data area of Node 35 |  |  |  | Read | 0xD500..0xD520
54784 | 32 |  | 64 | Data area of Node 36 |  |  |  | Read | 0xD600..0xD620
55040 | 32 |  | 64 | Data area of Node 37 |  |  |  | Read | 0xD700..0xD720
55296 | 32 |  | 64 | Data area of Node 38 |  |  |  | Read | 0xD800..0xD820
55552 | 32 |  | 64 | Data area of Node 39 |  |  |  | Read | 0xD900..0xD920
55808 | 32 |  | 64 | Data area of Node 40 |  |  |  | Read | 0xDA00..0xDA20
256 | 1 | 0 | 2 | modbus address | 1-247 | 1 | uint16 | Read/Write
257 | 1 | 2 | 2 | modbus baudrate | 0-1 | 0 | uint16 | Read/Write | 0: 9600, 1: 19200
258 | 1 | 4 | 2 | modbus parity | 0-2 | 0 | uint16 | Read/Write | 0: none, 1: odd, 2: even
259 | 9 | 6 | 18 | serial number |  |  | string | Read/Write(PW)
268 | 2 | 24 | 4 | password for setting |  |  | uint32 | Read/Write | Password = 190577
270 | 2 | 28 | 4 | con id |  |  | uint32 | Read/Write(PW)
272 | 1 | 32 | 2 | num of node | 0-40 |  | uint16 | Read/Write
273 | 80 | 34 | 160 | node id 1..40 |  |  | uint32 | Read/Write
353 | 1 | 194 | 2 | cmp time 1 |  | 15 | uint16 | Read/Write
354 | 1 | 196 | 2 | cmp time 2 |  | 30 | uint16 | Read/Write
355 | 1 | 198 | 2 | cmp time 3 |  | 45 | uint16 | Read/Write
356 | 1 | 200 | 2 | cmp time 4 |  | 60 | uint16 | Read/Write
357 | 1 | 202 | 2 | cmp time 5 |  | 300 | uint16 | Read/Write
358 | 1 | 204 | 2 | cmp time 6 |  | 600 | uint16 | Read/Write
359 | 1 | 206 | 2 | cmp time 7 |  | 900 | uint16 | Read/Write
360 | 1 | 208 | 2 | cmp time 8 |  | 1800 | uint16 | Read/Write
361 | 1 | 210 | 2 | cmp time 9 |  | 3600 | uint16 | Read/Write
362 | 37 | 212 | 74 | spare
399 | 1 | 286 | 2 | sync all node | 0-1 |  | uint16 | Read/Write | 1: restart sync
400 | 1200 | 288 | 2400 | node config 1..40 |  |  |  | Read/Write
Note:
+ update_enable_reg = 0xB601 = 46593 => update Cycle_wakeup, cycle_healthstatus of node (sensors)
+ update_enable_reg = 0xB680 = 46720 => update Data_numblock, data_reg, data_numreg of node
+ update_enable_reg = 0xB640 = 46656 => update Offset temp, humidity, pressure, analog value
+ update_enable_reg = 0xB620 = 46624 => update Delta temp, humidity, pressure
+ update_enable_reg = 0xB610 = 46608 => update CT for WS433-AC
+ update_enable_reg = 0xB608 = 46600 => update Cut-off for WS433-AC
+ password = 190577
READ: cmd 03
WRITE: cmd 16

## Chi tiết
Modbus Register (HEX) | Modbus Register (DEC) | # of register | Adr | Size | Description | Range | Default | Format | Property | Comment
0 | 0 | 2 | 0 | 4 | device info |  | STC1 | string | Read | Sensor tag receiver
2 | 2 | 4 | 4 | 8 | firmware version |  | 1.6 | string | Read
6 | 6 | 2 | 12 | 4 | hardware version |  | 2 | string | Read
8 | 8 | 1 | 16 | 2 | rssi node 1 & rssi node 2 |  |  | int8 | Read | rssi thực tế = rssi node - 256 (dBm)
9 | 9 | 1 | 18 | 2 | rssi node 3 & rssi node 4 |  |  | int8 | Read
A | 10 | 1 | 20 | 2 | rssi node 5 & rssi node 6 |  |  | int8 | Read
B | 11 | 1 | 22 | 2 | rssi node 7 & rssi node 8 |  |  | int8 | Read
C | 12 | 1 | 24 | 2 | rssi node 9 & rssi node 10 |  |  | int8 | Read
D | 13 | 1 | 26 | 2 | rssi node 11 & rssi node 12 |  |  | int8 | Read
E | 14 | 1 | 28 | 2 | rssi node 13 & rssi node 14 |  |  | int8 | Read
F | 15 | 1 | 30 | 2 | rssi node 15 & rssi node 16 |  |  | int8 | Read
10 | 16 | 1 | 32 | 2 | rssi node 17 & rssi node 18 |  |  | int8 | Read
11 | 17 | 1 | 34 | 2 | rssi node 19 & rssi node 20 |  |  | int8 | Read
12 | 18 | 1 | 36 | 2 | rssi node 21 & rssi node 22 |  |  | int8 | Read
13 | 19 | 1 | 38 | 2 | rssi node 23 & rssi node 24 |  |  | int8 | Read
14 | 20 | 1 | 40 | 2 | rssi node 25 & rssi node 26 |  |  | int8 | Read
15 | 21 | 1 | 42 | 2 | rssi node 27 & rssi node 28 |  |  | int8 | Read
16 | 22 | 1 | 44 | 2 | rssi node 29 & rssi node 30 |  |  | int8 | Read
17 | 23 | 1 | 46 | 2 | rssi node 31 & rssi node 32 |  |  | int8 | Read
18 | 24 | 1 | 48 | 2 | rssi node 33 & rssi node 34 |  |  | int8 | Read
19 | 25 | 1 | 50 | 2 | rssi node 35 & rssi node 36 |  |  | int8 | Read
1A | 26 | 1 | 52 | 2 | rssi node 37 & rssi node 38 |  |  | int8 | Read
1B | 27 | 1 | 54 | 2 | rssi node 39 & rssi node 40 |  |  | int8 | Read
1C | 28 | 1 | 56 | 2 | data status node 1 & data status node 2 | 0-9, 99 |  | uint8 | Read | + n = thời gian từ lúc nhận được data mới nhất của sensor đến hiện tại + data status = 99: khi chưa nhận được bất kỳ data nào 0: khi n <= cmp time 1 1: khi cmp time 1 < n <= cmp time 2 2: khi cmp time 2 < n <= cmp time 3 3: khi cmp time 3 < n <= cmp time 4 4: khi cmp time 4 < n <= cmp time 5 5: khi cmp time 5 < n <= cmp time 6 6: khi cmp time 6 < n <= cmp time 7 7: khi cmp time 7 < n <= cmp time 8 8: khi cmp time 8 < n <= cmp time 9 9: khi cmp time n > cmp time 9
1D | 29 | 1 | 58 | 2 | data status node 3 & data status node 4 | 0-9, 99 |  | uint8 | Read
1E | 30 | 1 | 60 | 2 | data status node 5 & data status node 6 | 0-9, 99 |  | uint8 | Read
1F | 31 | 1 | 62 | 2 | data status node 7 & data status node 8 | 0-9, 99 |  | uint8 | Read
20 | 32 | 1 | 64 | 2 | data status node 9 & data status node 10 | 0-9, 99 |  | uint8 | Read
21 | 33 | 1 | 66 | 2 | data status node 11 & data status node 12 | 0-9, 99 |  | uint8 | Read
22 | 34 | 1 | 68 | 2 | data status node 13 & data status node 14 | 0-9, 99 |  | uint8 | Read
23 | 35 | 1 | 70 | 2 | data status node 15 & data status node 16 | 0-9, 99 |  | uint8 | Read
24 | 36 | 1 | 72 | 2 | data status node 17 & data status node 18 | 0-9, 99 |  | uint8 | Read
25 | 37 | 1 | 74 | 2 | data status node 19 & data status node 20 | 0-9, 99 |  | uint8 | Read
26 | 38 | 1 | 76 | 2 | data status node 21 & data status node 22 | 0-9, 99 |  | uint8 | Read
27 | 39 | 1 | 78 | 2 | data status node 23 & data status node 24 | 0-9, 99 |  | uint8 | Read
28 | 40 | 1 | 80 | 2 | data status node 25 & data status node 26 | 0-9, 99 |  | uint8 | Read
29 | 41 | 1 | 82 | 2 | data status node 27 & data status node 28 | 0-9, 99 |  | uint8 | Read
2A | 42 | 1 | 84 | 2 | data status node 29 & data status node 30 | 0-9, 99 |  | uint8 | Read
2B | 43 | 1 | 86 | 2 | data status node 31 & data status node 32 | 0-9, 99 |  | uint8 | Read
2C | 44 | 1 | 88 | 2 | data status node 33 & data status node 34 | 0-9, 99 |  | uint8 | Read
2D | 45 | 1 | 90 | 2 | data status node 35 & data status node 36 | 0-9, 99 |  | uint8 | Read
2E | 46 | 1 | 92 | 2 | data status node 37 & data status node 38 | 0-9, 99 |  | uint8 | Read
2F | 47 | 1 | 94 | 2 | data status node 39 & data status node 40 | 0-9, 99 |  | uint8 | Read
30 | 48 | 1 | 96 | 2 | rf timeout count node 1 & rf timeout count node 2 |  |  | uint8 | Read | Tăng thêm 1 khi data status >=3
31 | 49 | 1 | 98 | 2 | rf timeout count node 3 & rf timeout count node 4 |  |  | uint8 | Read
32 | 50 | 1 | 100 | 2 | rf timeout count node 5 & rf timeout count node 6 |  |  | uint8 | Read
33 | 51 | 1 | 102 | 2 | rf timeout count node 7 & rf timeout count node 8 |  |  | uint8 | Read
34 | 52 | 1 | 104 | 2 | rf timeout count node 9 & rf timeout count node 10 |  |  | uint8 | Read
35 | 53 | 1 | 106 | 2 | rf timeout count node 11 & rf timeout count node 12 |  |  | uint8 | Read
36 | 54 | 1 | 108 | 2 | rf timeout count node 13 & rf timeout count node 14 |  |  | uint8 | Read
37 | 55 | 1 | 110 | 2 | rf timeout count node 15 & rf timeout count node 16 |  |  | uint8 | Read
38 | 56 | 1 | 112 | 2 | rf timeout count node 17 & rf timeout count node 18 |  |  | uint8 | Read
39 | 57 | 1 | 114 | 2 | rf timeout count node 19 & rf timeout count node 20 |  |  | uint8 | Read
3A | 58 | 1 | 116 | 2 | rf timeout count node 21 & rf timeout count node 22 |  |  | uint8 | Read
3B | 59 | 1 | 118 | 2 | rf timeout count node 23 & rf timeout count node 24 |  |  | uint8 | Read
3C | 60 | 1 | 120 | 2 | rf timeout count node 25 & rf timeout count node 26 |  |  | uint8 | Read
3D | 61 | 1 | 122 | 2 | rf timeout count node 27 & rf timeout count node 28 |  |  | uint8 | Read
3E | 62 | 1 | 124 | 2 | rf timeout count node 29 & rf timeout count node 30 |  |  | uint8 | Read
3F | 63 | 1 | 126 | 2 | rf timeout count node 31 & rf timeout count node 32 |  |  | uint8 | Read
40 | 64 | 1 | 128 | 2 | rf timeout count node 33 & rf timeout count node 34 |  |  | uint8 | Read
41 | 65 | 1 | 130 | 2 | rf timeout count node 35 & rf timeout count node 36 |  |  | uint8 | Read
42 | 66 | 1 | 132 | 2 | rf timeout count node 37 & rf timeout count node 38 |  |  | uint8 | Read
43 | 67 | 1 | 134 | 2 | rf timeout count node 39 & rf timeout count node 40 |  |  | uint8 | Read
44 | 68 | 1 | 136 | 2 | rssi status node 1 & rssi status node 2 | 0-4 |  | uint8 | Read | + RSSI = 0..-54dBm => RSSI Status = 4 (sóng RF mạnh nhất) + RSSI = -55..-69dBm => RSSI Status = 3 + RSSI = -70..-79dBm => RSSI Status = 2 + RSSI = -80..-100dBm => RSSI Status = 1 + RSSI < -100dBm => RSSI Status = 0
45 | 69 | 1 | 138 | 2 | rssi status node 3 & rssi status node 4 | 0-4 |  | uint8 | Read
46 | 70 | 1 | 140 | 2 | rssi status node 5 & rssi status node 6 | 0-4 |  | uint8 | Read
47 | 71 | 1 | 142 | 2 | rssi status node 7 & rssi status node 8 | 0-4 |  | uint8 | Read
48 | 72 | 1 | 144 | 2 | rssi status node 9 & rssi status node 10 | 0-4 |  | uint8 | Read
49 | 73 | 1 | 146 | 2 | rssi status node 11 & rssi status node 12 | 0-4 |  | uint8 | Read
4A | 74 | 1 | 148 | 2 | rssi status node 13 & rssi status node 14 | 0-4 |  | uint8 | Read
4B | 75 | 1 | 150 | 2 | rssi status node 15 & rssi status node 16 | 0-4 |  | uint8 | Read
4C | 76 | 1 | 152 | 2 | rssi status node 17 & rssi status node 18 | 0-4 |  | uint8 | Read
4D | 77 | 1 | 154 | 2 | rssi status node 19 & rssi status node 20 | 0-4 |  | uint8 | Read
4E | 78 | 1 | 156 | 2 | rssi status node 21 & rssi status node 22 | 0-4 |  | uint8 | Read
4F | 79 | 1 | 158 | 2 | rssi status node 23 & rssi status node 24 | 0-4 |  | uint8 | Read
50 | 80 | 1 | 160 | 2 | rssi status node 25 & rssi status node 26 | 0-4 |  | uint8 | Read
51 | 81 | 1 | 162 | 2 | rssi status node 27 & rssi status node 28 | 0-4 |  | uint8 | Read
52 | 82 | 1 | 164 | 2 | rssi status node 29 & rssi status node 30 | 0-4 |  | uint8 | Read
53 | 83 | 1 | 166 | 2 | rssi status node 31 & rssi status node 32 | 0-4 |  | uint8 | Read
54 | 84 | 1 | 168 | 2 | rssi status node 33 & rssi status node 34 | 0-4 |  | uint8 | Read
55 | 85 | 1 | 170 | 2 | rssi status node 35 & rssi status node 36 | 0-4 |  | uint8 | Read
56 | 86 | 1 | 172 | 2 | rssi status node 37 & rssi status node 38 | 0-4 |  | uint8 | Read
57 | 87 | 1 | 174 | 2 | rssi status node 39 & rssi status node 40 | 0-4 |  | uint8 | Read
58 | 88 | 60 | 176 | 120 | spare |  |  | uint8 | Read
94 | 148 | 1 | 296 | 2 | rx seq node 1 & rx seq node 2 |  |  | uint8 | Read
95 | 149 | 1 | 298 | 2 | rx seq node 3 & rx seq node 4 |  |  | uint8 | Read
96 | 150 | 1 | 300 | 2 | rx seq node 5 & rx seq node 6 |  |  | uint8 | Read
97 | 151 | 1 | 302 | 2 | rx seq node 7 & rx seq node 8 |  |  | uint8 | Read
98 | 152 | 1 | 304 | 2 | rx seq node 9 & rx seq node 10 |  |  | uint8 | Read
99 | 153 | 1 | 306 | 2 | rx seq node 11 & rx seq node 12 |  |  | uint8 | Read
9A | 154 | 1 | 308 | 2 | rx seq node 13 & rx seq node 14 |  |  | uint8 | Read
9B | 155 | 1 | 310 | 2 | rx seq node 15 & rx seq node 16 |  |  | uint8 | Read
9C | 156 | 1 | 312 | 2 | rx seq node 17 & rx seq node 18 |  |  | uint8 | Read
9D | 157 | 1 | 314 | 2 | rx seq node 19 & rx seq node 20 |  |  | uint8 | Read
9E | 158 | 1 | 316 | 2 | rx seq node 21 & rx seq node 22 |  |  | uint8 | Read
9F | 159 | 1 | 318 | 2 | rx seq node 23 & rx seq node 24 |  |  | uint8 | Read
A0 | 160 | 1 | 320 | 2 | rx seq node 25 & rx seq node 26 |  |  | uint8 | Read
A1 | 161 | 1 | 322 | 2 | rx seq node 27 & rx seq node 28 |  |  | uint8 | Read
A2 | 162 | 1 | 324 | 2 | rx seq node 29 & rx seq node 30 |  |  | uint8 | Read
A3 | 163 | 1 | 326 | 2 | rx seq node 31 & rx seq node 32 |  |  | uint8 | Read
A4 | 164 | 1 | 328 | 2 | rx seq node 33 & rx seq node 34 |  |  | uint8 | Read
A5 | 165 | 1 | 330 | 2 | rx seq node 35 & rx seq node 36 |  |  | uint8 | Read
A6 | 166 | 1 | 332 | 2 | rx seq node 37 & rx seq node 38 |  |  | uint8 | Read
A7 | 167 | 1 | 334 | 2 | rx seq node 39 & rx seq node 40 |  |  | uint8 | Read
A8 | 168 | 1 | 336 | 2 | rx duplication count node 1 & rx duplication count node 2 |  |  | uint8 | Read
A9 | 169 | 1 | 338 | 2 | rx duplication count node 3 & rx duplication count node 4 |  |  | uint8 | Read
AA | 170 | 1 | 340 | 2 | rx duplication count node 5 & rx duplication count node 6 |  |  | uint8 | Read
AB | 171 | 1 | 342 | 2 | rx duplication count node 7 & rx duplication count node 8 |  |  | uint8 | Read
AC | 172 | 1 | 344 | 2 | rx duplication count node 9 & rx duplication count node 10 |  |  | uint8 | Read
AD | 173 | 1 | 346 | 2 | rx duplication count node 11 & rx duplication count node 12 |  |  | uint8 | Read
AE | 174 | 1 | 348 | 2 | rx duplication count node 13 & rx duplication count node 14 |  |  | uint8 | Read
AF | 175 | 1 | 350 | 2 | rx duplication count node 15 & rx duplication count node 16 |  |  | uint8 | Read
B0 | 176 | 1 | 352 | 2 | rx duplication count node 17 & rx duplication count node 18 |  |  | uint8 | Read
B1 | 177 | 1 | 354 | 2 | rx duplication count node 19 & rx duplication count node 20 |  |  | uint8 | Read
B2 | 178 | 1 | 356 | 2 | rx duplication count node 21 & rx duplication count node 22 |  |  | uint8 | Read
B3 | 179 | 1 | 358 | 2 | rx duplication count node 23 & rx duplication count node 24 |  |  | uint8 | Read
B4 | 180 | 1 | 360 | 2 | rx duplication count node 25 & rx duplication count node 26 |  |  | uint8 | Read
B5 | 181 | 1 | 362 | 2 | rx duplication count node 27 & rx duplication count node 28 |  |  | uint8 | Read
B6 | 182 | 1 | 364 | 2 | rx duplication count node 29 & rx duplication count node 30 |  |  | uint8 | Read
B7 | 183 | 1 | 366 | 2 | rx duplication count node 31 & rx duplication count node 32 |  |  | uint8 | Read
B8 | 184 | 1 | 368 | 2 | rx duplication count node 33 & rx duplication count node 34 |  |  | uint8 | Read
B9 | 185 | 1 | 370 | 2 | rx duplication count node 35 & rx duplication count node 36 |  |  | uint8 | Read
BA | 186 | 1 | 372 | 2 | rx duplication count node 37 & rx duplication count node 38 |  |  | uint8 | Read
BB | 187 | 1 | 374 | 2 | rx duplication count node 39 & rx duplication count node 40 |  |  | uint8 | Read
BC | 188 | 1 | 376 | 2 | sync status node 1 & sync status node 2 | 0-2, 99 |  | uint8 | Read | 0: sync ok, 1: sync start, 2: cfg error, 99: nothing to sync
BD | 189 | 1 | 378 | 2 | sync status node 3 & sync status node 4 | 0-2, 99 |  | uint8 | Read
BE | 190 | 1 | 380 | 2 | sync status node 5 & sync status node 6 | 0-2, 99 |  | uint8 | Read
BF | 191 | 1 | 382 | 2 | sync status node 7 & sync status node 8 | 0-2, 99 |  | uint8 | Read
C0 | 192 | 1 | 384 | 2 | sync status node 9 & sync status node 10 | 0-2, 99 |  | uint8 | Read
C1 | 193 | 1 | 386 | 2 | sync status node 11 & sync status node 12 | 0-2, 99 |  | uint8 | Read
C2 | 194 | 1 | 388 | 2 | sync status node 13 & sync status node 14 | 0-2, 99 |  | uint8 | Read
C3 | 195 | 1 | 390 | 2 | sync status node 15 & sync status node 16 | 0-2, 99 |  | uint8 | Read
C4 | 196 | 1 | 392 | 2 | sync status node 17 & sync status node 18 | 0-2, 99 |  | uint8 | Read
C5 | 197 | 1 | 394 | 2 | sync status node 19 & sync status node 20 | 0-2, 99 |  | uint8 | Read
C6 | 198 | 1 | 396 | 2 | sync status node 21 & sync status node 22 | 0-2, 99 |  | uint8 | Read
C7 | 199 | 1 | 398 | 2 | sync status node 23 & sync status node 24 | 0-2, 99 |  | uint8 | Read
C8 | 200 | 1 | 400 | 2 | sync status node 25 & sync status node 26 | 0-2, 99 |  | uint8 | Read
C9 | 201 | 1 | 402 | 2 | sync status node 27 & sync status node 28 | 0-2, 99 |  | uint8 | Read
CA | 202 | 1 | 404 | 2 | sync status node 29 & sync status node 30 | 0-2, 99 |  | uint8 | Read
CB | 203 | 1 | 406 | 2 | sync status node 31 & sync status node 32 | 0-2, 99 |  | uint8 | Read
CC | 204 | 1 | 408 | 2 | sync status node 33 & sync status node 34 | 0-2, 99 |  | uint8 | Read
CD | 205 | 1 | 410 | 2 | sync status node 35 & sync status node 36 | 0-2, 99 |  | uint8 | Read
CE | 206 | 1 | 412 | 2 | sync status node 37 & sync status node 38 | 0-2, 99 |  | uint8 | Read
CF | 207 | 1 | 414 | 2 | sync status node 39 & sync status node 40 | 0-2, 99 |  | uint8 | Read
0
A100 | 41216 | 32 |  | 64 | Data area of Node 1 |  |  |  | Read | 0xA100..0xA120
A200 | 41472 | 32 |  | 64 | Data area of Node 2 |  |  |  | Read | 0xA200..0xA220
A300 | 41728 | 32 |  | 64 | Data area of Node 3 |  |  |  | Read | 0xA300..0xA320
A400 | 41984 | 32 |  | 64 | Data area of Node 4 |  |  |  | Read | 0xA400..0xA420
A500 | 42240 | 32 |  | 64 | Data area of Node 5 |  |  |  | Read | 0xA500..0xA520
A600 | 42496 | 32 |  | 64 | Data area of Node 6 |  |  |  | Read | 0xA600..0xA620
A700 | 42752 | 32 |  | 64 | Data area of Node 7 |  |  |  | Read | 0xA700..0xA720
A800 | 43008 | 32 |  | 64 | Data area of Node 8 |  |  |  | Read | 0xA800..0xA820
A900 | 43264 | 32 |  | 64 | Data area of Node 9 |  |  |  | Read | 0xA900..0xA920
AA00 | 43520 | 32 |  | 64 | Data area of Node 10 |  |  |  | Read | 0xAA00..0xAA20
B100 | 45312 | 32 |  | 64 | Data area of Node 11 |  |  |  | Read | 0xB100..0xB120
B200 | 45568 | 32 |  | 64 | Data area of Node 12 |  |  |  | Read | 0xB200..0xB220
B300 | 45824 | 32 |  | 64 | Data area of Node 13 |  |  |  | Read | 0xB300..0xB320
B400 | 46080 | 32 |  | 64 | Data area of Node 14 |  |  |  | Read | 0xB400..0xB420
B500 | 46336 | 32 |  | 64 | Data area of Node 15 |  |  |  | Read | 0xB500..0xB520
B600 | 46592 | 32 |  | 64 | Data area of Node 16 |  |  |  | Read | 0xB600..0xB620
B700 | 46848 | 32 |  | 64 | Data area of Node 17 |  |  |  | Read | 0xB700..0xB720
B800 | 47104 | 32 |  | 64 | Data area of Node 18 |  |  |  | Read | 0xB800..0xB820
B900 | 47360 | 32 |  | 64 | Data area of Node 19 |  |  |  | Read | 0xB900..0xB920
BA00 | 47616 | 32 |  | 64 | Data area of Node 20 |  |  |  | Read | 0xBA00..0xBA20
C100 | 49408 | 32 |  | 64 | Data area of Node 21 |  |  |  | Read | 0xC100..0xC120
C200 | 49664 | 32 |  | 64 | Data area of Node 22 |  |  |  | Read | 0xC200..0xC220
C300 | 49920 | 32 |  | 64 | Data area of Node 23 |  |  |  | Read | 0xC300..0xC320
C400 | 50176 | 32 |  | 64 | Data area of Node 24 |  |  |  | Read | 0xC400..0xC420
C500 | 50432 | 32 |  | 64 | Data area of Node 25 |  |  |  | Read | 0xC500..0xC520
C600 | 50688 | 32 |  | 64 | Data area of Node 26 |  |  |  | Read | 0xC600..0xC620
C700 | 50944 | 32 |  | 64 | Data area of Node 27 |  |  |  | Read | 0xC700..0xC720
C800 | 51200 | 32 |  | 64 | Data area of Node 28 |  |  |  | Read | 0xC800..0xC820
C900 | 51456 | 32 |  | 64 | Data area of Node 29 |  |  |  | Read | 0xC900..0xC920
CA00 | 51712 | 32 |  | 64 | Data area of Node 30 |  |  |  | Read | 0xCA00..0xCA20
D100 | 53504 | 32 |  | 64 | Data area of Node 31 |  |  |  | Read | 0xD100..0xD120
D200 | 53760 | 32 |  | 64 | Data area of Node 32 |  |  |  | Read | 0xD200..0xD220
D300 | 54016 | 32 |  | 64 | Data area of Node 33 |  |  |  | Read | 0xD300..0xD320
D400 | 54272 | 32 |  | 64 | Data area of Node 34 |  |  |  | Read | 0xD400..0xD420
D500 | 54528 | 32 |  | 64 | Data area of Node 35 |  |  |  | Read | 0xD500..0xD520
D600 | 54784 | 32 |  | 64 | Data area of Node 36 |  |  |  | Read | 0xD600..0xD620
D700 | 55040 | 32 |  | 64 | Data area of Node 37 |  |  |  | Read | 0xD700..0xD720
D800 | 55296 | 32 |  | 64 | Data area of Node 38 |  |  |  | Read | 0xD800..0xD820
D900 | 55552 | 32 |  | 64 | Data area of Node 39 |  |  |  | Read | 0xD900..0xD920
DA00 | 55808 | 32 |  | 64 | Data area of Node 40 |  |  |  | Read | 0xDA00..0xDA20
0
100 | 256 | 1 | 0 | 2 | modbus address | 1-247 | 1 | uint16 | Read/Write
101 | 257 | 1 | 2 | 2 | modbus baudrate | 0-1 | 0 | uint16 | Read/Write | 0: 9600, 1: 19200
102 | 258 | 1 | 4 | 2 | modbus parity | 0-2 | 0 | uint16 | Read/Write | 0: none, 1: odd, 2: even
103 | 259 | 9 | 6 | 18 | serial number |  |  | string | Read/Write(PW)
10C | 268 | 2 | 24 | 4 | password for setting |  |  | uint32 | Read/Write | Password = 190577
10E | 270 | 2 | 28 | 4 | receiver id |  |  | uint32 | Read/Write(PW)
110 | 272 | 1 | 32 | 2 | num of node | 0-40 |  | uint16 | Read/Write
111 | 273 | 2 | 34 | 4 | node id 1 |  |  | uint32 | Read/Write
113 | 275 | 2 | 38 | 4 | node id 2 |  |  | uint32 | Read/Write
115 | 277 | 2 | 42 | 4 | node id 3 |  |  | uint32 | Read/Write
117 | 279 | 2 | 46 | 4 | node id 4 |  |  | uint32 | Read/Write
119 | 281 | 2 | 50 | 4 | node id 5 |  |  | uint32 | Read/Write
11B | 283 | 2 | 54 | 4 | node id 6 |  |  | uint32 | Read/Write
11D | 285 | 2 | 58 | 4 | node id 7 |  |  | uint32 | Read/Write
11F | 287 | 2 | 62 | 4 | node id 8 |  |  | uint32 | Read/Write
121 | 289 | 2 | 66 | 4 | node id 9 |  |  | uint32 | Read/Write
123 | 291 | 2 | 70 | 4 | node id 10 |  |  | uint32 | Read/Write
125 | 293 | 2 | 74 | 4 | node id 11 |  |  | uint32 | Read/Write
127 | 295 | 2 | 78 | 4 | node id 12 |  |  | uint32 | Read/Write
129 | 297 | 2 | 82 | 4 | node id 13 |  |  | uint32 | Read/Write
12B | 299 | 2 | 86 | 4 | node id 14 |  |  | uint32 | Read/Write
12D | 301 | 2 | 90 | 4 | node id 15 |  |  | uint32 | Read/Write
12F | 303 | 2 | 94 | 4 | node id 16 |  |  | uint32 | Read/Write
131 | 305 | 2 | 98 | 4 | node id 17 |  |  | uint32 | Read/Write
133 | 307 | 2 | 102 | 4 | node id 18 |  |  | uint32 | Read/Write
135 | 309 | 2 | 106 | 4 | node id 19 |  |  | uint32 | Read/Write
137 | 311 | 2 | 110 | 4 | node id 20 |  |  | uint32 | Read/Write
139 | 313 | 2 | 114 | 4 | node id 21 |  |  | uint32 | Read/Write
13B | 315 | 2 | 118 | 4 | node id 22 |  |  | uint32 | Read/Write
13D | 317 | 2 | 122 | 4 | node id 23 |  |  | uint32 | Read/Write
13F | 319 | 2 | 126 | 4 | node id 24 |  |  | uint32 | Read/Write
141 | 321 | 2 | 130 | 4 | node id 25 |  |  | uint32 | Read/Write
143 | 323 | 2 | 134 | 4 | node id 26 |  |  | uint32 | Read/Write
145 | 325 | 2 | 138 | 4 | node id 27 |  |  | uint32 | Read/Write
147 | 327 | 2 | 142 | 4 | node id 28 |  |  | uint32 | Read/Write
149 | 329 | 2 | 146 | 4 | node id 29 |  |  | uint32 | Read/Write
14B | 331 | 2 | 150 | 4 | node id 30 |  |  | uint32 | Read/Write
14D | 333 | 2 | 154 | 4 | node id 31 |  |  | uint32 | Read/Write
14F | 335 | 2 | 158 | 4 | node id 32 |  |  | uint32 | Read/Write
151 | 337 | 2 | 162 | 4 | node id 33 |  |  | uint32 | Read/Write
153 | 339 | 2 | 166 | 4 | node id 34 |  |  | uint32 | Read/Write
155 | 341 | 2 | 170 | 4 | node id 35 |  |  | uint32 | Read/Write
157 | 343 | 2 | 174 | 4 | node id 36 |  |  | uint32 | Read/Write
159 | 345 | 2 | 178 | 4 | node id 37 |  |  | uint32 | Read/Write
15B | 347 | 2 | 182 | 4 | node id 38 |  |  | uint32 | Read/Write
15D | 349 | 2 | 186 | 4 | node id 39 |  |  | uint32 | Read/Write
15F | 351 | 2 | 190 | 4 | node id 40 |  |  | uint32 | Read/Write
161 | 353 | 1 | 194 | 2 | cmp time 1 |  | 15 | uint16 | Read/Write | second
162 | 354 | 1 | 196 | 2 | cmp time 2 |  | 30 | uint16 | Read/Write | second
163 | 355 | 1 | 198 | 2 | cmp time 3 |  | 45 | uint16 | Read/Write | second
164 | 356 | 1 | 200 | 2 | cmp time 4 |  | 60 | uint16 | Read/Write | second
165 | 357 | 1 | 202 | 2 | cmp time 5 |  | 300 | uint16 | Read/Write | second
166 | 358 | 1 | 204 | 2 | cmp time 6 |  | 600 | uint16 | Read/Write | second
167 | 359 | 1 | 206 | 2 | cmp time 7 |  | 900 | uint16 | Read/Write | second
168 | 360 | 1 | 208 | 2 | cmp time 8 |  | 1800 | uint16 | Read/Write | second
169 | 361 | 1 | 210 | 2 | cmp time 9 |  | 3600 | uint16 | Read/Write | second
16A | 362 | 37 | 212 | 74 | spare
18F | 399 | 1 | 286 | 2 | sync all node | 0-1 |  | uint16 | Read/Write | 1: restart sync
190 | 400 | 1 | 288 | 2 | Update_enable_Node1 |  |  | hex | Read/Write | + update enable = 0xB601 = 46593 => update Cycle_wakeup, cycle_healthstatus of node + update enable = 0xB680 = 46720 => update Data_numblock, data_reg, data_numreg of node + update enable = 0xB640 = 46656 => update Offset temp, humidity, pulse width 4 channel of node + update enable = 0xB620 = 46624 => update Delta temp, humidity, counter of node
191 | 401 | 1 | 290 | 2 | Cycle_wakeup_Node1 |  |  | uint16 | Read/Write
192 | 402 | 1 | 292 | 2 | Cycle_heathsta_Node1 |  |  | uint16 | Read/Write
193 | 403 | 1 | 294 | 2 | Data_numblock_Node1 |  |  | uint16 | Read/Write
194 | 404 | 1 | 296 | 2 | Data_reg 1_Node1 |  |  | uint16 | Read/Write
195 | 405 | 1 | 298 | 2 | Data_numreg 1_Node1 |  |  | uint16 | Read/Write
196 | 406 | 1 | 300 | 2 | Data_reg 2_Node1 |  |  | uint16 | Read/Write
197 | 407 | 1 | 302 | 2 | Data_numReg 2_Node1 |  |  | uint16 | Read/Write
198 | 408 | 1 | 304 | 2 | Data_reg 3_Node1 |  |  | uint16 | Read/Write
199 | 409 | 1 | 306 | 2 | Data_numReg 3_Node1 |  |  | uint16 | Read/Write
19A | 410 | 20 | 308 | 40 | Reserve_regs_Node1 |  |  |  | Read/Write | reserve registers for node 1= 20 regs = 40 bytes
1AE | 430 | 1 | 348 | 2 | Update_enable_Node2 |  |  | hex | Read/Write
1AF | 431 | 1 | 350 | 2 | Cycle_wakeup_Node2 |  |  | uint16 | Read/Write
1B0 | 432 | 1 | 352 | 2 | Cycle_heathsta_Node2 |  |  | uint16 | Read/Write
1B1 | 433 | 1 | 354 | 2 | Data_numblock_Node2 |  |  | uint16 | Read/Write
1B2 | 434 | 1 | 356 | 2 | Data_reg 1_Node2 |  |  | uint16 | Read/Write
1B3 | 435 | 1 | 358 | 2 | Data_numreg 1_Node2 |  |  | uint16 | Read/Write
1B4 | 436 | 1 | 360 | 2 | Data_reg 2_Node2 |  |  | uint16 | Read/Write
1B5 | 437 | 1 | 362 | 2 | Data_numReg 2_Node2 |  |  | uint16 | Read/Write
1B6 | 438 | 1 | 364 | 2 | Data_reg 3_Node2 |  |  | uint16 | Read/Write
1B7 | 439 | 1 | 366 | 2 | Data_numReg 3_Node2 |  |  | uint16 | Read/Write
1B8 | 440 | 20 | 368 | 40 | Reserve_regs_Node2 |  |  |  | Read/Write | reserve registers for node 2 = 20 regs = 40 bytes
1CC | 460 | 1 | 408 | 2 | Update_enable_Node3 |  |  | hex | Read/Write
1CD | 461 | 1 | 410 | 2 | Cycle_wakeup_Node3 |  |  | uint16 | Read/Write
1CE | 462 | 1 | 412 | 2 | Cycle_heathsta_Node3 |  |  | uint16 | Read/Write
1CF | 463 | 1 | 414 | 2 | Data_numblock_Node3 |  |  | uint16 | Read/Write
1D0 | 464 | 1 | 416 | 2 | Data_reg 1_Node3 |  |  | uint16 | Read/Write
1D1 | 465 | 1 | 418 | 2 | Data_numreg 1_Node3 |  |  | uint16 | Read/Write
1D2 | 466 | 1 | 420 | 2 | Data_reg 2_Node3 |  |  | uint16 | Read/Write
1D3 | 467 | 1 | 422 | 2 | Data_numReg 2_Node3 |  |  | uint16 | Read/Write
1D4 | 468 | 1 | 424 | 2 | Data_reg 3_Node3 |  |  | uint16 | Read/Write
1D5 | 469 | 1 | 426 | 2 | Data_numReg 3_Node3 |  |  | uint16 | Read/Write
1D6 | 470 | 20 | 428 | 40 | Reserve_regs_Node3 |  |  |  | Read/Write | reserve registers for node 3 = 20 regs = 40 bytes
1EA | 490 | 1 | 468 | 2 | Update_enable_Node4 |  |  | hex | Read/Write
1EB | 491 | 1 | 470 | 2 | Cycle_wakeup_Node4 |  |  | uint16 | Read/Write
1EC | 492 | 1 | 472 | 2 | Cycle_heathsta_Node4 |  |  | uint16 | Read/Write
1ED | 493 | 1 | 474 | 2 | Data_numblock_Node4 |  |  | uint16 | Read/Write
1EE | 494 | 1 | 476 | 2 | Data_reg 1_Node4 |  |  | uint16 | Read/Write
1EF | 495 | 1 | 478 | 2 | Data_numreg 1_Node4 |  |  | uint16 | Read/Write
1F0 | 496 | 1 | 480 | 2 | Data_reg 2_Node4 |  |  | uint16 | Read/Write
1F1 | 497 | 1 | 482 | 2 | Data_numReg 2_Node4 |  |  | uint16 | Read/Write
1F2 | 498 | 1 | 484 | 2 | Data_reg 3_Node4 |  |  | uint16 | Read/Write
1F3 | 499 | 1 | 486 | 2 | Data_numReg 3_Node4 |  |  | uint16 | Read/Write
1F4 | 500 | 20 | 488 | 40 | Reserve_regs_Node4 |  |  |  | Read/Write | reserve registers for node 4 = 20 regs = 40 bytes
208 | 520 | 1 | 528 | 2 | Update_enable_Node5 |  |  | hex | Read/Write
209 | 521 | 1 | 530 | 2 | Cycle_wakeup_Node5 |  |  | uint16 | Read/Write
20A | 522 | 1 | 532 | 2 | Cycle_heathsta_Node5 |  |  | uint16 | Read/Write
20B | 523 | 1 | 534 | 2 | Data_numblock_Node5 |  |  | uint16 | Read/Write
20C | 524 | 1 | 536 | 2 | Data_reg 1_Node5 |  |  | uint16 | Read/Write
20D | 525 | 1 | 538 | 2 | Data_numreg 1_Node5 |  |  | uint16 | Read/Write
20E | 526 | 1 | 540 | 2 | Data_reg 2_Node5 |  |  | uint16 | Read/Write
20F | 527 | 1 | 542 | 2 | Data_numReg 2_Node5 |  |  | uint16 | Read/Write
210 | 528 | 1 | 544 | 2 | Data_reg 3_Node5 |  |  | uint16 | Read/Write
211 | 529 | 1 | 546 | 2 | Data_numReg 3_Node5 |  |  | uint16 | Read/Write
212 | 530 | 20 | 548 | 40 | Reserve_regs_Node5 |  |  |  | Read/Write | reserve registers for node 5 = 20 regs = 40 bytes
226 | 550 | 1 | 588 | 2 | Update_enable_Node6 |  |  | hex | Read/Write
227 | 551 | 1 | 590 | 2 | Cycle_wakeup_Node6 |  |  | uint16 | Read/Write
228 | 552 | 1 | 592 | 2 | Cycle_heathsta_Node6 |  |  | uint16 | Read/Write
229 | 553 | 1 | 594 | 2 | Data_numblock_Node6 |  |  | uint16 | Read/Write
22A | 554 | 1 | 596 | 2 | Data_reg 1_Node6 |  |  | uint16 | Read/Write
22B | 555 | 1 | 598 | 2 | Data_numreg 1_Node6 |  |  | uint16 | Read/Write
22C | 556 | 1 | 600 | 2 | Data_reg 2_Node6 |  |  | uint16 | Read/Write
22D | 557 | 1 | 602 | 2 | Data_numReg 2_Node6 |  |  | uint16 | Read/Write
22E | 558 | 1 | 604 | 2 | Data_reg 3_Node6 |  |  | uint16 | Read/Write
22F | 559 | 1 | 606 | 2 | Data_numReg 3_Node6 |  |  | uint16 | Read/Write
230 | 560 | 20 | 608 | 40 | Reserve_regs_Node6 |  |  |  | Read/Write | reserve registers for node 6 = 20 regs = 40 bytes
244 | 580 | 1 | 648 | 2 | Update_enable_Node7 |  |  | hex | Read/Write
245 | 581 | 1 | 650 | 2 | Cycle_wakeup_Node7 |  |  | uint16 | Read/Write
246 | 582 | 1 | 652 | 2 | Cycle_heathsta_Node7 |  |  | uint16 | Read/Write
247 | 583 | 1 | 654 | 2 | Data_numblock_Node7 |  |  | uint16 | Read/Write
248 | 584 | 1 | 656 | 2 | Data_reg 1_Node7 |  |  | uint16 | Read/Write
249 | 585 | 1 | 658 | 2 | Data_numreg 1_Node7 |  |  | uint16 | Read/Write
24A | 586 | 1 | 660 | 2 | Data_reg 2_Node7 |  |  | uint16 | Read/Write
24B | 587 | 1 | 662 | 2 | Data_numReg 2_Node7 |  |  | uint16 | Read/Write
24C | 588 | 1 | 664 | 2 | Data_reg 3_Node7 |  |  | uint16 | Read/Write
24D | 589 | 1 | 666 | 2 | Data_numReg 3_Node7 |  |  | uint16 | Read/Write
24E | 590 | 20 | 668 | 40 | Reserve_regs_Node7 |  |  |  | Read/Write | reserve registers for node 7 = 20 regs = 40 bytes
262 | 610 | 1 | 708 | 2 | Update_enable_Node8 |  |  | hex | Read/Write
263 | 611 | 1 | 710 | 2 | Cycle_wakeup_Node8 |  |  | uint16 | Read/Write
264 | 612 | 1 | 712 | 2 | Cycle_heathsta_Node8 |  |  | uint16 | Read/Write
265 | 613 | 1 | 714 | 2 | Data_numblock_Node8 |  |  | uint16 | Read/Write
266 | 614 | 1 | 716 | 2 | Data_reg 1_Node8 |  |  | uint16 | Read/Write
267 | 615 | 1 | 718 | 2 | Data_numreg 1_Node8 |  |  | uint16 | Read/Write
268 | 616 | 1 | 720 | 2 | Data_reg 2_Node8 |  |  | uint16 | Read/Write
269 | 617 | 1 | 722 | 2 | Data_numReg 2_Node8 |  |  | uint16 | Read/Write
26A | 618 | 1 | 724 | 2 | Data_reg 3_Node8 |  |  | uint16 | Read/Write
26B | 619 | 1 | 726 | 2 | Data_numReg 3_Node8 |  |  | uint16 | Read/Write
26C | 620 | 20 | 728 | 40 | Reserve_regs_Node8 |  |  |  | Read/Write | reserve registers for node 8 = 20 regs = 40 bytes
280 | 640 | 1 | 768 | 2 | Update_enable_Node9 |  |  | hex | Read/Write
281 | 641 | 1 | 770 | 2 | Cycle_wakeup_Node9 |  |  | uint16 | Read/Write
282 | 642 | 1 | 772 | 2 | Cycle_heathsta_Node9 |  |  | uint16 | Read/Write
283 | 643 | 1 | 774 | 2 | Data_numblock_Node9 |  |  | uint16 | Read/Write
284 | 644 | 1 | 776 | 2 | Data_reg 1_Node9 |  |  | uint16 | Read/Write
285 | 645 | 1 | 778 | 2 | Data_numreg 1_Node9 |  |  | uint16 | Read/Write
286 | 646 | 1 | 780 | 2 | Data_reg 2_Node9 |  |  | uint16 | Read/Write
287 | 647 | 1 | 782 | 2 | Data_numReg 2_Node9 |  |  | uint16 | Read/Write
288 | 648 | 1 | 784 | 2 | Data_reg 3_Node9 |  |  | uint16 | Read/Write
289 | 649 | 1 | 786 | 2 | Data_numReg 3_Node9 |  |  | uint16 | Read/Write
28A | 650 | 20 | 788 | 40 | Reserve_regs_Node9 |  |  |  | Read/Write | reserve registers for node 9 = 20 regs = 40 bytes
29E | 670 | 1 | 828 | 2 | Update_enable_Node10 |  |  | hex | Read/Write
29F | 671 | 1 | 830 | 2 | Cycle_wakeup_Node10 |  |  | uint16 | Read/Write
2A0 | 672 | 1 | 832 | 2 | Cycle_heathsta_Node10 |  |  | uint16 | Read/Write
2A1 | 673 | 1 | 834 | 2 | Data_numblock_Node10 |  |  | uint16 | Read/Write
2A2 | 674 | 1 | 836 | 2 | Data_reg 1_Node10 |  |  | uint16 | Read/Write
2A3 | 675 | 1 | 838 | 2 | Data_numreg 1_Node10 |  |  | uint16 | Read/Write
2A4 | 676 | 1 | 840 | 2 | Data_reg 2_Node10 |  |  | uint16 | Read/Write
2A5 | 677 | 1 | 842 | 2 | Data_numReg 2_Node10 |  |  | uint16 | Read/Write
2A6 | 678 | 1 | 844 | 2 | Data_reg 3_Node10 |  |  | uint16 | Read/Write
2A7 | 679 | 1 | 846 | 2 | Data_numReg 3_Node10 |  |  | uint16 | Read/Write
2A8 | 680 | 20 | 848 | 40 | Reserve_regs_Node10 |  |  |  | Read/Write | reserve registers for node 10 = 20 regs = 40 bytes
2BC | 700 | 1 | 888 | 2 | Update_enable_Node11 |  |  | hex | Read/Write
2BD | 701 | 1 | 890 | 2 | Cycle_wakeup_Node11 |  |  | uint16 | Read/Write
2BE | 702 | 1 | 892 | 2 | Cycle_heathsta_Node11 |  |  | uint16 | Read/Write
2BF | 703 | 1 | 894 | 2 | Data_numblock_Node11 |  |  | uint16 | Read/Write
2C0 | 704 | 1 | 896 | 2 | Data_reg 1_Node11 |  |  | uint16 | Read/Write
2C1 | 705 | 1 | 898 | 2 | Data_numreg 1_Node11 |  |  | uint16 | Read/Write
2C2 | 706 | 1 | 900 | 2 | Data_reg 2_Node11 |  |  | uint16 | Read/Write
2C3 | 707 | 1 | 902 | 2 | Data_numReg 2_Node11 |  |  | uint16 | Read/Write
2C4 | 708 | 1 | 904 | 2 | Data_reg 3_Node11 |  |  | uint16 | Read/Write
2C5 | 709 | 1 | 906 | 2 | Data_numReg 3_Node11 |  |  | uint16 | Read/Write
2C6 | 710 | 20 | 908 | 40 | Reserve_regs_Node11 |  |  |  | Read/Write | reserve registers for node 11 = 20 regs = 40 bytes
2DA | 730 | 1 | 948 | 2 | Update_enable_Node12 |  |  | hex | Read/Write
2DB | 731 | 1 | 950 | 2 | Cycle_wakeup_Node12 |  |  | uint16 | Read/Write
2DC | 732 | 1 | 952 | 2 | Cycle_heathsta_Node12 |  |  | uint16 | Read/Write
2DD | 733 | 1 | 954 | 2 | Data_numblock_Node12 |  |  | uint16 | Read/Write
2DE | 734 | 1 | 956 | 2 | Data_reg 1_Node12 |  |  | uint16 | Read/Write
2DF | 735 | 1 | 958 | 2 | Data_numreg 1_Node12 |  |  | uint16 | Read/Write
2E0 | 736 | 1 | 960 | 2 | Data_reg 2_Node12 |  |  | uint16 | Read/Write
2E1 | 737 | 1 | 962 | 2 | Data_numReg 2_Node12 |  |  | uint16 | Read/Write
2E2 | 738 | 1 | 964 | 2 | Data_reg 3_Node12 |  |  | uint16 | Read/Write
2E3 | 739 | 1 | 966 | 2 | Data_numReg 3_Node12 |  |  | uint16 | Read/Write
2E4 | 740 | 20 | 968 | 40 | Reserve_regs_Node12 |  |  |  | Read/Write | reserve registers for node 12 = 20 regs = 40 bytes
2F8 | 760 | 1 | 1008 | 2 | Update_enable_Node13 |  |  | hex | Read/Write
2F9 | 761 | 1 | 1010 | 2 | Cycle_wakeup_Node13 |  |  | uint16 | Read/Write
2FA | 762 | 1 | 1012 | 2 | Cycle_heathsta_Node13 |  |  | uint16 | Read/Write
2FB | 763 | 1 | 1014 | 2 | Data_numblock_Node13 |  |  | uint16 | Read/Write
2FC | 764 | 1 | 1016 | 2 | Data_reg 1_Node13 |  |  | uint16 | Read/Write
2FD | 765 | 1 | 1018 | 2 | Data_numreg 1_Node13 |  |  | uint16 | Read/Write
2FE | 766 | 1 | 1020 | 2 | Data_reg 2_Node13 |  |  | uint16 | Read/Write
2FF | 767 | 1 | 1022 | 2 | Data_numReg 2_Node13 |  |  | uint16 | Read/Write
300 | 768 | 1 | 1024 | 2 | Data_reg 3_Node13 |  |  | uint16 | Read/Write
301 | 769 | 1 | 1026 | 2 | Data_numReg 3_Node13 |  |  | uint16 | Read/Write
302 | 770 | 20 | 1028 | 40 | Reserve_regs_Node13 |  |  |  | Read/Write | reserve registers for node 13 = 20 regs = 40 bytes
316 | 790 | 1 | 1068 | 2 | Update_enable_Node14 |  |  | hex | Read/Write
317 | 791 | 1 | 1070 | 2 | Cycle_wakeup_Node14 |  |  | uint16 | Read/Write
318 | 792 | 1 | 1072 | 2 | Cycle_heathsta_Node14 |  |  | uint16 | Read/Write
319 | 793 | 1 | 1074 | 2 | Data_numblock_Node14 |  |  | uint16 | Read/Write
31A | 794 | 1 | 1076 | 2 | Data_reg 1_Node14 |  |  | uint16 | Read/Write
31B | 795 | 1 | 1078 | 2 | Data_numreg 1_Node14 |  |  | uint16 | Read/Write
31C | 796 | 1 | 1080 | 2 | Data_reg 2_Node14 |  |  | uint16 | Read/Write
31D | 797 | 1 | 1082 | 2 | Data_numReg 2_Node14 |  |  | uint16 | Read/Write
31E | 798 | 1 | 1084 | 2 | Data_reg 3_Node14 |  |  | uint16 | Read/Write
31F | 799 | 1 | 1086 | 2 | Data_numReg 3_Node14 |  |  | uint16 | Read/Write
320 | 800 | 20 | 1088 | 40 | Reserve_regs_Node14 |  |  |  | Read/Write | reserve registers for node 14 = 20 regs = 40 bytes
334 | 820 | 1 | 1128 | 2 | Update_enable_Node15 |  |  | hex | Read/Write
335 | 821 | 1 | 1130 | 2 | Cycle_wakeup_Node15 |  |  | uint16 | Read/Write
336 | 822 | 1 | 1132 | 2 | Cycle_heathsta_Node15 |  |  | uint16 | Read/Write
337 | 823 | 1 | 1134 | 2 | Data_numblock_Node15 |  |  | uint16 | Read/Write
338 | 824 | 1 | 1136 | 2 | Data_reg 1_Node15 |  |  | uint16 | Read/Write
339 | 825 | 1 | 1138 | 2 | Data_numreg 1_Node15 |  |  | uint16 | Read/Write
33A | 826 | 1 | 1140 | 2 | Data_reg 2_Node15 |  |  | uint16 | Read/Write
33B | 827 | 1 | 1142 | 2 | Data_numReg 2_Node15 |  |  | uint16 | Read/Write
33C | 828 | 1 | 1144 | 2 | Data_reg 3_Node15 |  |  | uint16 | Read/Write
33D | 829 | 1 | 1146 | 2 | Data_numReg 3_Node15 |  |  | uint16 | Read/Write
33E | 830 | 20 | 1148 | 40 | Reserve_regs_Node15 |  |  |  | Read/Write | reserve registers for node 15 = 20 regs = 40 bytes
352 | 850 | 1 | 1188 | 2 | Update_enable_Node16 |  |  | hex | Read/Write
353 | 851 | 1 | 1190 | 2 | Cycle_wakeup_Node16 |  |  | uint16 | Read/Write
354 | 852 | 1 | 1192 | 2 | Cycle_heathsta_Node16 |  |  | uint16 | Read/Write
355 | 853 | 1 | 1194 | 2 | Data_numblock_Node16 |  |  | uint16 | Read/Write
356 | 854 | 1 | 1196 | 2 | Data_reg 1_Node16 |  |  | uint16 | Read/Write
357 | 855 | 1 | 1198 | 2 | Data_numreg 1_Node16 |  |  | uint16 | Read/Write
358 | 856 | 1 | 1200 | 2 | Data_reg 2_Node16 |  |  | uint16 | Read/Write
359 | 857 | 1 | 1202 | 2 | Data_numReg 2_Node16 |  |  | uint16 | Read/Write
35A | 858 | 1 | 1204 | 2 | Data_reg 3_Node16 |  |  | uint16 | Read/Write
35B | 859 | 1 | 1206 | 2 | Data_numReg 3_Node16 |  |  | uint16 | Read/Write
35C | 860 | 20 | 1208 | 40 | Reserve_regs_Node16 |  |  |  | Read/Write | reserve registers for node 16 = 20 regs = 40 bytes
370 | 880 | 1 | 1248 | 2 | Update_enable_Node17 |  |  | hex | Read/Write
371 | 881 | 1 | 1250 | 2 | Cycle_wakeup_Node17 |  |  | uint16 | Read/Write
372 | 882 | 1 | 1252 | 2 | Cycle_heathsta_Node17 |  |  | uint16 | Read/Write
373 | 883 | 1 | 1254 | 2 | Data_numblock_Node17 |  |  | uint16 | Read/Write
374 | 884 | 1 | 1256 | 2 | Data_reg 1_Node17 |  |  | uint16 | Read/Write
375 | 885 | 1 | 1258 | 2 | Data_numreg 1_Node17 |  |  | uint16 | Read/Write
376 | 886 | 1 | 1260 | 2 | Data_reg 2_Node17 |  |  | uint16 | Read/Write
377 | 887 | 1 | 1262 | 2 | Data_numReg 2_Node17 |  |  | uint16 | Read/Write
378 | 888 | 1 | 1264 | 2 | Data_reg 3_Node17 |  |  | uint16 | Read/Write
379 | 889 | 1 | 1266 | 2 | Data_numReg 3_Node17 |  |  | uint16 | Read/Write
37A | 890 | 20 | 1268 | 40 | Reserve_regs_Node17 |  |  |  | Read/Write | reserve registers for node 17 = 20 regs = 40 bytes
38E | 910 | 1 | 1308 | 2 | Update_enable_Node18 |  |  | hex | Read/Write
38F | 911 | 1 | 1310 | 2 | Cycle_wakeup_Node18 |  |  | uint16 | Read/Write
390 | 912 | 1 | 1312 | 2 | Cycle_heathsta_Node18 |  |  | uint16 | Read/Write
391 | 913 | 1 | 1314 | 2 | Data_numblock_Node18 |  |  | uint16 | Read/Write
392 | 914 | 1 | 1316 | 2 | Data_reg 1_Node18 |  |  | uint16 | Read/Write
393 | 915 | 1 | 1318 | 2 | Data_numreg 1_Node18 |  |  | uint16 | Read/Write
394 | 916 | 1 | 1320 | 2 | Data_reg 2_Node18 |  |  | uint16 | Read/Write
395 | 917 | 1 | 1322 | 2 | Data_numReg 2_Node18 |  |  | uint16 | Read/Write
396 | 918 | 1 | 1324 | 2 | Data_reg 3_Node18 |  |  | uint16 | Read/Write
397 | 919 | 1 | 1326 | 2 | Data_numReg 3_Node18 |  |  | uint16 | Read/Write
398 | 920 | 20 | 1328 | 40 | Reserve_regs_Node18 |  |  |  | Read/Write | reserve registers for node 18 = 20 regs = 40 bytes
3AC | 940 | 1 | 1368 | 2 | Update_enable_Node19 |  |  | hex | Read/Write
3AD | 941 | 1 | 1370 | 2 | Cycle_wakeup_Node19 |  |  | uint16 | Read/Write
3AE | 942 | 1 | 1372 | 2 | Cycle_heathsta_Node19 |  |  | uint16 | Read/Write
3AF | 943 | 1 | 1374 | 2 | Data_numblock_Node19 |  |  | uint16 | Read/Write
3B0 | 944 | 1 | 1376 | 2 | Data_reg 1_Node19 |  |  | uint16 | Read/Write
3B1 | 945 | 1 | 1378 | 2 | Data_numreg 1_Node19 |  |  | uint16 | Read/Write
3B2 | 946 | 1 | 1380 | 2 | Data_reg 2_Node19 |  |  | uint16 | Read/Write
3B3 | 947 | 1 | 1382 | 2 | Data_numReg 2_Node19 |  |  | uint16 | Read/Write
3B4 | 948 | 1 | 1384 | 2 | Data_reg 3_Node19 |  |  | uint16 | Read/Write
3B5 | 949 | 1 | 1386 | 2 | Data_numReg 3_Node19 |  |  | uint16 | Read/Write
3B6 | 950 | 20 | 1388 | 40 | Reserve_regs_Node19 |  |  |  | Read/Write | reserve registers for node 19 = 20 regs = 40 bytes
3CA | 970 | 1 | 1428 | 2 | Update_enable_Node20 |  |  | hex | Read/Write
3CB | 971 | 1 | 1430 | 2 | Cycle_wakeup_Node20 |  |  | uint16 | Read/Write
3CC | 972 | 1 | 1432 | 2 | Cycle_heathsta_Node20 |  |  | uint16 | Read/Write
3CD | 973 | 1 | 1434 | 2 | Data_numblock_Node20 |  |  | uint16 | Read/Write
3CE | 974 | 1 | 1436 | 2 | Data_reg 1_Node20 |  |  | uint16 | Read/Write
3CF | 975 | 1 | 1438 | 2 | Data_numreg 1_Node20 |  |  | uint16 | Read/Write
3D0 | 976 | 1 | 1440 | 2 | Data_reg 2_Node20 |  |  | uint16 | Read/Write
3D1 | 977 | 1 | 1442 | 2 | Data_numReg 2_Node20 |  |  | uint16 | Read/Write
3D2 | 978 | 1 | 1444 | 2 | Data_reg 3_Node20 |  |  | uint16 | Read/Write
3D3 | 979 | 1 | 1446 | 2 | Data_numReg 3_Node20 |  |  | uint16 | Read/Write
3D4 | 980 | 20 | 1448 | 40 | Reserve_regs_Node20 |  |  |  | Read/Write | reserve registers for node 20 = 20 regs = 40 bytes
3E8 | 1000 | 1 | 1488 | 2 | Update_enable_Node21 |  |  | hex | Read/Write
3E9 | 1001 | 1 | 1490 | 2 | Cycle_wakeup_Node21 |  |  | uint16 | Read/Write
3EA | 1002 | 1 | 1492 | 2 | Cycle_heathsta_Node21 |  |  | uint16 | Read/Write
3EB | 1003 | 1 | 1494 | 2 | Data_numblock_Node21 |  |  | uint16 | Read/Write
3EC | 1004 | 1 | 1496 | 2 | Data_reg 1_Node21 |  |  | uint16 | Read/Write
3ED | 1005 | 1 | 1498 | 2 | Data_numreg 1_Node21 |  |  | uint16 | Read/Write
3EE | 1006 | 1 | 1500 | 2 | Data_reg 2_Node21 |  |  | uint16 | Read/Write
3EF | 1007 | 1 | 1502 | 2 | Data_numReg 2_Node21 |  |  | uint16 | Read/Write
3F0 | 1008 | 1 | 1504 | 2 | Data_reg 3_Node21 |  |  | uint16 | Read/Write
3F1 | 1009 | 1 | 1506 | 2 | Data_numReg 3_Node21 |  |  | uint16 | Read/Write
3F2 | 1010 | 20 | 1508 | 40 | Reserve_regs_Node21 |  |  |  | Read/Write | reserve registers for node 21 = 20 regs = 40 bytes
406 | 1030 | 1 | 1548 | 2 | Update_enable_Node22 |  |  | hex | Read/Write
407 | 1031 | 1 | 1550 | 2 | Cycle_wakeup_Node22 |  |  | uint16 | Read/Write
408 | 1032 | 1 | 1552 | 2 | Cycle_heathsta_Node22 |  |  | uint16 | Read/Write
409 | 1033 | 1 | 1554 | 2 | Data_numblock_Node22 |  |  | uint16 | Read/Write
40A | 1034 | 1 | 1556 | 2 | Data_reg 1_Node22 |  |  | uint16 | Read/Write
40B | 1035 | 1 | 1558 | 2 | Data_numreg 1_Node22 |  |  | uint16 | Read/Write
40C | 1036 | 1 | 1560 | 2 | Data_reg 2_Node22 |  |  | uint16 | Read/Write
40D | 1037 | 1 | 1562 | 2 | Data_numReg 2_Node22 |  |  | uint16 | Read/Write
40E | 1038 | 1 | 1564 | 2 | Data_reg 3_Node22 |  |  | uint16 | Read/Write
40F | 1039 | 1 | 1566 | 2 | Data_numReg 3_Node22 |  |  | uint16 | Read/Write
410 | 1040 | 20 | 1568 | 40 | Reserve_regs_Node22 |  |  |  | Read/Write | reserve registers for node 22 = 20 regs = 40 bytes
424 | 1060 | 1 | 1608 | 2 | Update_enable_Node23 |  |  | hex | Read/Write
425 | 1061 | 1 | 1610 | 2 | Cycle_wakeup_Node23 |  |  | uint16 | Read/Write
426 | 1062 | 1 | 1612 | 2 | Cycle_heathsta_Node23 |  |  | uint16 | Read/Write
427 | 1063 | 1 | 1614 | 2 | Data_numblock_Node23 |  |  | uint16 | Read/Write
428 | 1064 | 1 | 1616 | 2 | Data_reg 1_Node23 |  |  | uint16 | Read/Write
429 | 1065 | 1 | 1618 | 2 | Data_numreg 1_Node23 |  |  | uint16 | Read/Write
42A | 1066 | 1 | 1620 | 2 | Data_reg 2_Node23 |  |  | uint16 | Read/Write
42B | 1067 | 1 | 1622 | 2 | Data_numReg 2_Node23 |  |  | uint16 | Read/Write
42C | 1068 | 1 | 1624 | 2 | Data_reg 3_Node23 |  |  | uint16 | Read/Write
42D | 1069 | 1 | 1626 | 2 | Data_numReg 3_Node23 |  |  | uint16 | Read/Write
42E | 1070 | 20 | 1628 | 40 | Reserve_regs_Node23 |  |  |  | Read/Write | reserve registers for node 23 = 20 regs = 40 bytes
442 | 1090 | 1 | 1668 | 2 | Update_enable_Node24 |  |  | hex | Read/Write
443 | 1091 | 1 | 1670 | 2 | Cycle_wakeup_Node24 |  |  | uint16 | Read/Write
444 | 1092 | 1 | 1672 | 2 | Cycle_heathsta_Node24 |  |  | uint16 | Read/Write
445 | 1093 | 1 | 1674 | 2 | Data_numblock_Node24 |  |  | uint16 | Read/Write
446 | 1094 | 1 | 1676 | 2 | Data_reg 1_Node24 |  |  | uint16 | Read/Write
447 | 1095 | 1 | 1678 | 2 | Data_numreg 1_Node24 |  |  | uint16 | Read/Write
448 | 1096 | 1 | 1680 | 2 | Data_reg 2_Node24 |  |  | uint16 | Read/Write
449 | 1097 | 1 | 1682 | 2 | Data_numReg 2_Node24 |  |  | uint16 | Read/Write
44A | 1098 | 1 | 1684 | 2 | Data_reg 3_Node24 |  |  | uint16 | Read/Write
44B | 1099 | 1 | 1686 | 2 | Data_numReg 3_Node24 |  |  | uint16 | Read/Write
44C | 1100 | 20 | 1688 | 40 | Reserve_regs_Node24 |  |  |  | Read/Write | reserve registers for node 24 = 20 regs = 40 bytes
460 | 1120 | 1 | 1728 | 2 | Update_enable_Node25 |  |  | hex | Read/Write
461 | 1121 | 1 | 1730 | 2 | Cycle_wakeup_Node25 |  |  | uint16 | Read/Write
462 | 1122 | 1 | 1732 | 2 | Cycle_heathsta_Node25 |  |  | uint16 | Read/Write
463 | 1123 | 1 | 1734 | 2 | Data_numblock_Node25 |  |  | uint16 | Read/Write
464 | 1124 | 1 | 1736 | 2 | Data_reg 1_Node25 |  |  | uint16 | Read/Write
465 | 1125 | 1 | 1738 | 2 | Data_numreg 1_Node25 |  |  | uint16 | Read/Write
466 | 1126 | 1 | 1740 | 2 | Data_reg 2_Node25 |  |  | uint16 | Read/Write
467 | 1127 | 1 | 1742 | 2 | Data_numReg 2_Node25 |  |  | uint16 | Read/Write
468 | 1128 | 1 | 1744 | 2 | Data_reg 3_Node25 |  |  | uint16 | Read/Write
469 | 1129 | 1 | 1746 | 2 | Data_numReg 3_Node25 |  |  | uint16 | Read/Write
46A | 1130 | 20 | 1748 | 40 | Reserve_regs_Node25 |  |  |  | Read/Write | reserve registers for node 25 = 20 regs = 40 bytes
47E | 1150 | 1 | 1788 | 2 | Update_enable_Node26 |  |  | hex | Read/Write
47F | 1151 | 1 | 1790 | 2 | Cycle_wakeup_Node26 |  |  | uint16 | Read/Write
480 | 1152 | 1 | 1792 | 2 | Cycle_heathsta_Node26 |  |  | uint16 | Read/Write
481 | 1153 | 1 | 1794 | 2 | Data_numblock_Node26 |  |  | uint16 | Read/Write
482 | 1154 | 1 | 1796 | 2 | Data_reg 1_Node26 |  |  | uint16 | Read/Write
483 | 1155 | 1 | 1798 | 2 | Data_numreg 1_Node26 |  |  | uint16 | Read/Write
484 | 1156 | 1 | 1800 | 2 | Data_reg 2_Node26 |  |  | uint16 | Read/Write
485 | 1157 | 1 | 1802 | 2 | Data_numReg 2_Node26 |  |  | uint16 | Read/Write
486 | 1158 | 1 | 1804 | 2 | Data_reg 3_Node26 |  |  | uint16 | Read/Write
487 | 1159 | 1 | 1806 | 2 | Data_numReg 3_Node26 |  |  | uint16 | Read/Write
488 | 1160 | 20 | 1808 | 40 | Reserve_regs_Node26 |  |  |  | Read/Write | reserve registers for node 26 = 20 regs = 40 bytes
49C | 1180 | 1 | 1848 | 2 | Update_enable_Node27 |  |  | hex | Read/Write
49D | 1181 | 1 | 1850 | 2 | Cycle_wakeup_Node27 |  |  | uint16 | Read/Write
49E | 1182 | 1 | 1852 | 2 | Cycle_heathsta_Node27 |  |  | uint16 | Read/Write
49F | 1183 | 1 | 1854 | 2 | Data_numblock_Node27 |  |  | uint16 | Read/Write
4A0 | 1184 | 1 | 1856 | 2 | Data_reg 1_Node27 |  |  | uint16 | Read/Write
4A1 | 1185 | 1 | 1858 | 2 | Data_numreg 1_Node27 |  |  | uint16 | Read/Write
4A2 | 1186 | 1 | 1860 | 2 | Data_reg 2_Node27 |  |  | uint16 | Read/Write
4A3 | 1187 | 1 | 1862 | 2 | Data_numReg 2_Node27 |  |  | uint16 | Read/Write
4A4 | 1188 | 1 | 1864 | 2 | Data_reg 3_Node27 |  |  | uint16 | Read/Write
4A5 | 1189 | 1 | 1866 | 2 | Data_numReg 3_Node27 |  |  | uint16 | Read/Write
4A6 | 1190 | 20 | 1868 | 40 | Reserve_regs_Node27 |  |  |  | Read/Write | reserve registers for node 27 = 20 regs = 40 bytes
4BA | 1210 | 1 | 1908 | 2 | Update_enable_Node28 |  |  | hex | Read/Write
4BB | 1211 | 1 | 1910 | 2 | Cycle_wakeup_Node28 |  |  | uint16 | Read/Write
4BC | 1212 | 1 | 1912 | 2 | Cycle_heathsta_Node28 |  |  | uint16 | Read/Write
4BD | 1213 | 1 | 1914 | 2 | Data_numblock_Node28 |  |  | uint16 | Read/Write
4BE | 1214 | 1 | 1916 | 2 | Data_reg 1_Node28 |  |  | uint16 | Read/Write
4BF | 1215 | 1 | 1918 | 2 | Data_numreg 1_Node28 |  |  | uint16 | Read/Write
4C0 | 1216 | 1 | 1920 | 2 | Data_reg 2_Node28 |  |  | uint16 | Read/Write
4C1 | 1217 | 1 | 1922 | 2 | Data_numReg 2_Node28 |  |  | uint16 | Read/Write
4C2 | 1218 | 1 | 1924 | 2 | Data_reg 3_Node28 |  |  | uint16 | Read/Write
4C3 | 1219 | 1 | 1926 | 2 | Data_numReg 3_Node28 |  |  | uint16 | Read/Write
4C4 | 1220 | 20 | 1928 | 40 | Reserve_regs_Node28 |  |  |  | Read/Write | reserve registers for node 28 = 20 regs = 40 bytes
4D8 | 1240 | 1 | 1968 | 2 | Update_enable_Node29 |  |  | hex | Read/Write
4D9 | 1241 | 1 | 1970 | 2 | Cycle_wakeup_Node29 |  |  | uint16 | Read/Write
4DA | 1242 | 1 | 1972 | 2 | Cycle_heathsta_Node29 |  |  | uint16 | Read/Write
4DB | 1243 | 1 | 1974 | 2 | Data_numblock_Node29 |  |  | uint16 | Read/Write
4DC | 1244 | 1 | 1976 | 2 | Data_reg 1_Node29 |  |  | uint16 | Read/Write
4DD | 1245 | 1 | 1978 | 2 | Data_numreg 1_Node29 |  |  | uint16 | Read/Write
4DE | 1246 | 1 | 1980 | 2 | Data_reg 2_Node29 |  |  | uint16 | Read/Write
4DF | 1247 | 1 | 1982 | 2 | Data_numReg 2_Node29 |  |  | uint16 | Read/Write
4E0 | 1248 | 1 | 1984 | 2 | Data_reg 3_Node29 |  |  | uint16 | Read/Write
4E1 | 1249 | 1 | 1986 | 2 | Data_numReg 3_Node29 |  |  | uint16 | Read/Write
4E2 | 1250 | 20 | 1988 | 40 | Reserve_regs_Node29 |  |  |  | Read/Write | reserve registers for node 29 = 20 regs = 40 bytes
4F6 | 1270 | 1 | 2028 | 2 | Update_enable_Node30 |  |  | hex | Read/Write
4F7 | 1271 | 1 | 2030 | 2 | Cycle_wakeup_Node30 |  |  | uint16 | Read/Write
4F8 | 1272 | 1 | 2032 | 2 | Cycle_heathsta_Node30 |  |  | uint16 | Read/Write
4F9 | 1273 | 1 | 2034 | 2 | Data_numblock_Node30 |  |  | uint16 | Read/Write
4FA | 1274 | 1 | 2036 | 2 | Data_reg 1_Node30 |  |  | uint16 | Read/Write
4FB | 1275 | 1 | 2038 | 2 | Data_numreg 1_Node30 |  |  | uint16 | Read/Write
4FC | 1276 | 1 | 2040 | 2 | Data_reg 2_Node30 |  |  | uint16 | Read/Write
4FD | 1277 | 1 | 2042 | 2 | Data_numReg 2_Node30 |  |  | uint16 | Read/Write
4FE | 1278 | 1 | 2044 | 2 | Data_reg 3_Node30 |  |  | uint16 | Read/Write
4FF | 1279 | 1 | 2046 | 2 | Data_numReg 3_Node30 |  |  | uint16 | Read/Write
500 | 1280 | 20 | 2048 | 40 | Reserve_regs_Node30 |  |  |  | Read/Write | reserve registers for node 30 = 20 regs = 40 bytes
514 | 1300 | 1 | 2088 | 2 | Update_enable_Node31 |  |  | hex | Read/Write
515 | 1301 | 1 | 2090 | 2 | Cycle_wakeup_Node31 |  |  | uint16 | Read/Write
516 | 1302 | 1 | 2092 | 2 | Cycle_heathsta_Node31 |  |  | uint16 | Read/Write
517 | 1303 | 1 | 2094 | 2 | Data_numblock_Node31 |  |  | uint16 | Read/Write
518 | 1304 | 1 | 2096 | 2 | Data_reg 1_Node31 |  |  | uint16 | Read/Write
519 | 1305 | 1 | 2098 | 2 | Data_numreg 1_Node31 |  |  | uint16 | Read/Write
51A | 1306 | 1 | 2100 | 2 | Data_reg 2_Node31 |  |  | uint16 | Read/Write
51B | 1307 | 1 | 2102 | 2 | Data_numReg 2_Node31 |  |  | uint16 | Read/Write
51C | 1308 | 1 | 2104 | 2 | Data_reg 3_Node31 |  |  | uint16 | Read/Write
51D | 1309 | 1 | 2106 | 2 | Data_numReg 3_Node31 |  |  | uint16 | Read/Write
51E | 1310 | 20 | 2108 | 40 | Reserve_regs_Node31 |  |  |  | Read/Write | reserve registers for node 31= 20 regs = 40 bytes
532 | 1330 | 1 | 2148 | 2 | Update_enable_Node32 |  |  | hex | Read/Write
533 | 1331 | 1 | 2150 | 2 | Cycle_wakeup_Node32 |  |  | uint16 | Read/Write
534 | 1332 | 1 | 2152 | 2 | Cycle_heathsta_Node32 |  |  | uint16 | Read/Write
535 | 1333 | 1 | 2154 | 2 | Data_numblock_Node32 |  |  | uint16 | Read/Write
536 | 1334 | 1 | 2156 | 2 | Data_reg 1_Node32 |  |  | uint16 | Read/Write
537 | 1335 | 1 | 2158 | 2 | Data_numreg 1_Node32 |  |  | uint16 | Read/Write
538 | 1336 | 1 | 2160 | 2 | Data_reg 2_Node32 |  |  | uint16 | Read/Write
539 | 1337 | 1 | 2162 | 2 | Data_numReg 2_Node32 |  |  | uint16 | Read/Write
53A | 1338 | 1 | 2164 | 2 | Data_reg 3_Node32 |  |  | uint16 | Read/Write
53B | 1339 | 1 | 2166 | 2 | Data_numReg 3_Node32 |  |  | uint16 | Read/Write
53C | 1340 | 20 | 2168 | 40 | Reserve_regs_Node32 |  |  |  | Read/Write | reserve registers for node 32 = 20 regs = 40 bytes
550 | 1360 | 1 | 2208 | 2 | Update_enable_Node33 |  |  | hex | Read/Write
551 | 1361 | 1 | 2210 | 2 | Cycle_wakeup_Node33 |  |  | uint16 | Read/Write
552 | 1362 | 1 | 2212 | 2 | Cycle_heathsta_Node33 |  |  | uint16 | Read/Write
553 | 1363 | 1 | 2214 | 2 | Data_numblock_Node33 |  |  | uint16 | Read/Write
554 | 1364 | 1 | 2216 | 2 | Data_reg 1_Node33 |  |  | uint16 | Read/Write
555 | 1365 | 1 | 2218 | 2 | Data_numreg 1_Node33 |  |  | uint16 | Read/Write
556 | 1366 | 1 | 2220 | 2 | Data_reg 2_Node33 |  |  | uint16 | Read/Write
557 | 1367 | 1 | 2222 | 2 | Data_numReg 2_Node33 |  |  | uint16 | Read/Write
558 | 1368 | 1 | 2224 | 2 | Data_reg 3_Node33 |  |  | uint16 | Read/Write
559 | 1369 | 1 | 2226 | 2 | Data_numReg 3_Node33 |  |  | uint16 | Read/Write
55A | 1370 | 20 | 2228 | 40 | Reserve_regs_Node33 |  |  |  | Read/Write | reserve registers for node 33 = 20 regs = 40 bytes
56E | 1390 | 1 | 2268 | 2 | Update_enable_Node34 |  |  | hex | Read/Write
56F | 1391 | 1 | 2270 | 2 | Cycle_wakeup_Node34 |  |  | uint16 | Read/Write
570 | 1392 | 1 | 2272 | 2 | Cycle_heathsta_Node34 |  |  | uint16 | Read/Write
571 | 1393 | 1 | 2274 | 2 | Data_numblock_Node34 |  |  | uint16 | Read/Write
572 | 1394 | 1 | 2276 | 2 | Data_reg 1_Node34 |  |  | uint16 | Read/Write
573 | 1395 | 1 | 2278 | 2 | Data_numreg 1_Node34 |  |  | uint16 | Read/Write
574 | 1396 | 1 | 2280 | 2 | Data_reg 2_Node34 |  |  | uint16 | Read/Write
575 | 1397 | 1 | 2282 | 2 | Data_numReg 2_Node34 |  |  | uint16 | Read/Write
576 | 1398 | 1 | 2284 | 2 | Data_reg 3_Node34 |  |  | uint16 | Read/Write
577 | 1399 | 1 | 2286 | 2 | Data_numReg 3_Node34 |  |  | uint16 | Read/Write
578 | 1400 | 20 | 2288 | 40 | Reserve_regs_Node34 |  |  |  | Read/Write | reserve registers for node 34 = 20 regs = 40 bytes
58C | 1420 | 1 | 2328 | 2 | Update_enable_Node35 |  |  | hex | Read/Write
58D | 1421 | 1 | 2330 | 2 | Cycle_wakeup_Node35 |  |  | uint16 | Read/Write
58E | 1422 | 1 | 2332 | 2 | Cycle_heathsta_Node35 |  |  | uint16 | Read/Write
58F | 1423 | 1 | 2334 | 2 | Data_numblock_Node35 |  |  | uint16 | Read/Write
590 | 1424 | 1 | 2336 | 2 | Data_reg 1_Node35 |  |  | uint16 | Read/Write
591 | 1425 | 1 | 2338 | 2 | Data_numreg 1_Node35 |  |  | uint16 | Read/Write
592 | 1426 | 1 | 2340 | 2 | Data_reg 2_Node35 |  |  | uint16 | Read/Write
593 | 1427 | 1 | 2342 | 2 | Data_numReg 2_Node35 |  |  | uint16 | Read/Write
594 | 1428 | 1 | 2344 | 2 | Data_reg 3_Node35 |  |  | uint16 | Read/Write
595 | 1429 | 1 | 2346 | 2 | Data_numReg 3_Node35 |  |  | uint16 | Read/Write
596 | 1430 | 20 | 2348 | 40 | Reserve_regs_Node35 |  |  |  | Read/Write | reserve registers for node 35 = 20 regs = 40 bytes
5AA | 1450 | 1 | 2388 | 2 | Update_enable_Node36 |  |  | hex | Read/Write
5AB | 1451 | 1 | 2390 | 2 | Cycle_wakeup_Node36 |  |  | uint16 | Read/Write
5AC | 1452 | 1 | 2392 | 2 | Cycle_heathsta_Node36 |  |  | uint16 | Read/Write
5AD | 1453 | 1 | 2394 | 2 | Data_numblock_Node36 |  |  | uint16 | Read/Write
5AE | 1454 | 1 | 2396 | 2 | Data_reg 1_Node36 |  |  | uint16 | Read/Write
5AF | 1455 | 1 | 2398 | 2 | Data_numreg 1_Node36 |  |  | uint16 | Read/Write
5B0 | 1456 | 1 | 2400 | 2 | Data_reg 2_Node36 |  |  | uint16 | Read/Write
5B1 | 1457 | 1 | 2402 | 2 | Data_numReg 2_Node36 |  |  | uint16 | Read/Write
5B2 | 1458 | 1 | 2404 | 2 | Data_reg 3_Node36 |  |  | uint16 | Read/Write
5B3 | 1459 | 1 | 2406 | 2 | Data_numReg 3_Node36 |  |  | uint16 | Read/Write
5B4 | 1460 | 20 | 2408 | 40 | Reserve_regs_Node36 |  |  |  | Read/Write | reserve registers for node 36 = 20 regs = 40 bytes
5C8 | 1480 | 1 | 2448 | 2 | Update_enable_Node37 |  |  | hex | Read/Write
5C9 | 1481 | 1 | 2450 | 2 | Cycle_wakeup_Node37 |  |  | uint16 | Read/Write
5CA | 1482 | 1 | 2452 | 2 | Cycle_heathsta_Node37 |  |  | uint16 | Read/Write
5CB | 1483 | 1 | 2454 | 2 | Data_numblock_Node37 |  |  | uint16 | Read/Write
5CC | 1484 | 1 | 2456 | 2 | Data_reg 1_Node37 |  |  | uint16 | Read/Write
5CD | 1485 | 1 | 2458 | 2 | Data_numreg 1_Node37 |  |  | uint16 | Read/Write
5CE | 1486 | 1 | 2460 | 2 | Data_reg 2_Node37 |  |  | uint16 | Read/Write
5CF | 1487 | 1 | 2462 | 2 | Data_numReg 2_Node37 |  |  | uint16 | Read/Write
5D0 | 1488 | 1 | 2464 | 2 | Data_reg 3_Node37 |  |  | uint16 | Read/Write
5D1 | 1489 | 1 | 2466 | 2 | Data_numReg 3_Node37 |  |  | uint16 | Read/Write
5D2 | 1490 | 20 | 2468 | 40 | Reserve_regs_Node37 |  |  |  | Read/Write | reserve registers for node 37 = 20 regs = 40 bytes
5E6 | 1510 | 1 | 2508 | 2 | Update_enable_Node38 |  |  | hex | Read/Write
5E7 | 1511 | 1 | 2510 | 2 | Cycle_wakeup_Node38 |  |  | uint16 | Read/Write
5E8 | 1512 | 1 | 2512 | 2 | Cycle_heathsta_Node38 |  |  | uint16 | Read/Write
5E9 | 1513 | 1 | 2514 | 2 | Data_numblock_Node38 |  |  | uint16 | Read/Write
5EA | 1514 | 1 | 2516 | 2 | Data_reg 1_Node38 |  |  | uint16 | Read/Write
5EB | 1515 | 1 | 2518 | 2 | Data_numreg 1_Node38 |  |  | uint16 | Read/Write
5EC | 1516 | 1 | 2520 | 2 | Data_reg 2_Node38 |  |  | uint16 | Read/Write
5ED | 1517 | 1 | 2522 | 2 | Data_numReg 2_Node38 |  |  | uint16 | Read/Write
5EE | 1518 | 1 | 2524 | 2 | Data_reg 3_Node38 |  |  | uint16 | Read/Write
5EF | 1519 | 1 | 2526 | 2 | Data_numReg 3_Node38 |  |  | uint16 | Read/Write
5F0 | 1520 | 20 | 2528 | 40 | Reserve_regs_Node38 |  |  |  | Read/Write | reserve registers for node 38 = 20 regs = 40 bytes
604 | 1540 | 1 | 2568 | 2 | Update_enable_Node39 |  |  | hex | Read/Write
605 | 1541 | 1 | 2570 | 2 | Cycle_wakeup_Node39 |  |  | uint16 | Read/Write
606 | 1542 | 1 | 2572 | 2 | Cycle_heathsta_Node39 |  |  | uint16 | Read/Write
607 | 1543 | 1 | 2574 | 2 | Data_numblock_Node39 |  |  | uint16 | Read/Write
608 | 1544 | 1 | 2576 | 2 | Data_reg 1_Node39 |  |  | uint16 | Read/Write
609 | 1545 | 1 | 2578 | 2 | Data_numreg 1_Node39 |  |  | uint16 | Read/Write
60A | 1546 | 1 | 2580 | 2 | Data_reg 2_Node39 |  |  | uint16 | Read/Write
60B | 1547 | 1 | 2582 | 2 | Data_numReg 2_Node39 |  |  | uint16 | Read/Write
60C | 1548 | 1 | 2584 | 2 | Data_reg 3_Node39 |  |  | uint16 | Read/Write
60D | 1549 | 1 | 2586 | 2 | Data_numReg 3_Node39 |  |  | uint16 | Read/Write
60E | 1550 | 20 | 2588 | 40 | Reserve_regs_Node39 |  |  |  | Read/Write | reserve registers for node 39 = 20 regs = 40 bytes
622 | 1570 | 1 | 2628 | 2 | Update_enable_Node40 |  |  | hex | Read/Write
623 | 1571 | 1 | 2630 | 2 | Cycle_wakeup_Node40 |  |  | uint16 | Read/Write
624 | 1572 | 1 | 2632 | 2 | Cycle_heathsta_Node40 |  |  | uint16 | Read/Write
625 | 1573 | 1 | 2634 | 2 | Data_numblock_Node40 |  |  | uint16 | Read/Write
626 | 1574 | 1 | 2636 | 2 | Data_reg 1_Node40 |  |  | uint16 | Read/Write
627 | 1575 | 1 | 2638 | 2 | Data_numreg 1_Node40 |  |  | uint16 | Read/Write
628 | 1576 | 1 | 2640 | 2 | Data_reg 2_Node40 |  |  | uint16 | Read/Write
629 | 1577 | 1 | 2642 | 2 | Data_numReg 2_Node40 |  |  | uint16 | Read/Write
62A | 1578 | 1 | 2644 | 2 | Data_reg 3_Node40 |  |  | uint16 | Read/Write
62B | 1579 | 1 | 2646 | 2 | Data_numReg 3_Node40 |  |  | uint16 | Read/Write
62C | 1580 | 20 | 2648 | 40 | Reserve_regs_Node40 |  |  |  | Read/Write | reserve registers for node 40 = 20 regs = 40 bytes
Note:
+ update_enable_reg = 0xB601 = 46593 => update Cycle_wakeup, cycle_healthstatus of node (sensors)
+ update_enable_reg = 0xB680 = 46720 => update Data_numblock, data_reg, data_numreg of node
+ update_enable_reg = 0xB640 = 46656 => update Offset temp, humidity, pressure, analog value
+ update_enable_reg = 0xB620 = 46624 => update Delta temp, humidity, pressure
+ update_enable_reg = 0xB610 = 46608 => update CT for WS433-AC
+ update_enable_reg = 0xB608 = 46600 => update Cut-off for WS433-AC
+ password = 190577
READ: cmd 03
WRITE: cmd 16

## Data area of sensor là Temp.
Modbus Register | # of register | Adr | Size | Description | Range | Default | Format | Property | Comment
41216 | 1 |  | 2 | %Battery Node1 | 10,30,60,99 |  | uint16 | Read | Wireless Sensor là loại cảm biến nhiệt độ, 0xA100..0xA120
41217 | 2 |  | 4 | Temperature Node1 | oC |  | float | Read | oC = -40..+125oC
41219 | 1 |  | 2 | Status Node 1 | 0-255 |  | uint16 | Read | Ý nghĩa status của sensor 1: + Status = 0: không có cảm biến or cảm biến hư + Status = 1: cảm biến nhiệt độ + Status = 2: cảm biến độ ẩm + Status = 3: cảm biến chênh áp môi trường + Status = 4: cảm biến áp suất … Status = n: cảm biến + Status = 255: đã thay đổi loại cảm biến mà chưa reset để nhận dạng cảm biến mới + Status = 254: sensor port chạm GND + Status = 253: sensor port chạm Vcc + Status = 252: sensor port chạm nhau
41472 | 1 |  | 2 | %Battery Node2 | 10,30,60,99 |  | uint16 | Read | 0xA200..0xA220
41473 | 2 |  | 4 | Temperature Node2 | oC |  | float | Read
41475 | 1 |  | 2 | Status Node 2 | 0-255 |  | uint16 | Read
41728 | 1 |  | 2 | %Battery Node3 | 10,30,60,99 |  | uint16 | Read | 0xA300..0xA320
41729 | 2 |  | 4 | Temperature Node3 | oC |  | float | Read
41731 | 1 |  | 2 | Status Node 3 | 0-255 |  | uint16 | Read
41984 | 1 |  | 2 | %Battery Node4 | 10,30,60,99 |  | uint16 | Read | 0xA400..0xA420
41985 | 2 |  | 4 | Temperature Node4 | oC |  | float | Read
41987 | 1 |  | 2 | Status Node 4 | 0-255 |  | uint16 | Read
42240 | 1 |  | 2 | %Battery Node5 | 10,30,60,99 |  | uint16 | Read | 0xA500..0xA520
42241 | 2 |  | 4 | Temperature Node5 | oC |  | float | Read
42243 | 1 |  | 2 | Status Node 5 | 0-255 |  | uint16 | Read
42496 | 1 |  | 2 | %Battery Node6 | 10,30,60,99 |  | uint16 | Read | 0xA600..0xA620
42497 | 2 |  | 4 | Temperature Node6 | oC |  | float | Read
42499 | 1 |  | 2 | Status Node 6 | 0-255 |  | uint16 | Read
42752 | 1 |  | 2 | %Battery Node7 | 10,30,60,99 |  | uint16 | Read | 0xA700..0xA720
42753 | 2 |  | 4 | Temperature Node7 | oC |  | float | Read
42755 | 1 |  | 2 | Status Node 7 | 0-255 |  | uint16 | Read
43008 | 1 |  | 2 | %Battery Node8 | 10,30,60,99 |  | uint16 | Read | 0xA800..0xA820
43009 | 2 |  | 4 | Temperature Node8 | oC |  | float | Read
43011 | 1 |  | 2 | Status Node 8 | 0-255 |  | uint16 | Read
43264 | 1 |  | 2 | %Battery Node9 | 10,30,60,99 |  | uint16 | Read | 0xA900..0xA920
43265 | 2 |  | 4 | Temperature Node9 | oC |  | float | Read
43267 | 1 |  | 2 | Status Node 9 | 0-255 |  | uint16 | Read
43520 | 1 |  | 2 | %Battery Node10 | 10,30,60,99 |  | uint16 | Read | 0xAA00..0xAA20
43521 | 2 |  | 4 | Temperature Node10 | oC |  | float | Read
43523 | 1 |  | 2 | Status Node 10 | 0-255 |  | uint16 | Read
45312 | 1 |  | 2 | %Battery Node11 | 10,30,60,99 |  | uint16 | Read | 0xB100..0xB120
45313 | 2 |  | 4 | Temperature Node11 | oC |  | float | Read
45315 | 1 |  | 2 | Status Node 11 | 0-255 |  | uint16 | Read
45568 | 1 |  | 2 | %Battery Node12 | 10,30,60,99 |  | uint16 | Read | 0xB200..0xB220
45569 | 2 |  | 4 | Temperature Node12 | oC |  | float | Read
45571 | 1 |  | 2 | Status Node 12 | 0-255 |  | uint16 | Read
45824 | 1 |  | 2 | %Battery Node13 | 10,30,60,99 |  | uint16 | Read | 0xB300..0xB320
45825 | 2 |  | 4 | Temperature Node13 | oC |  | float | Read
45827 | 1 |  | 2 | Status Node 13 | 0-255 |  | uint16 | Read
46080 | 1 |  | 2 | %Battery Node14 | 10,30,60,99 |  | uint16 | Read | 0xB400..0xB420
46081 | 2 |  | 4 | Temperature Node14 | oC |  | float | Read
46083 | 1 |  | 2 | Status Node 14 | 0-255 |  | uint16 | Read
46336 | 1 |  | 2 | %Battery Node15 | 10,30,60,99 |  | uint16 | Read | 0xB500..0xB520
46337 | 2 |  | 4 | Temperature Node15 | oC |  | float | Read
46339 | 1 |  | 2 | Status Node 15 | 0-255 |  | uint16 | Read
46592 | 1 |  | 2 | %Battery Node16 | 10,30,60,99 |  | uint16 | Read | 0xB600..0xB620
46593 | 2 |  | 4 | Temperature Node16 | oC |  | float | Read
46595 | 1 |  | 2 | Status Node 16 | 0-255 |  | uint16 | Read
46848 | 1 |  | 2 | %Battery Node17 | 10,30,60,99 |  | uint16 | Read | 0xB700..0xB720
46849 | 2 |  | 4 | Temperature Node17 | oC |  | float | Read
46851 | 1 |  | 2 | Status Node 17 | 0-255 |  | uint16 | Read
47104 | 1 |  | 2 | %Battery Node18 | 10,30,60,99 |  | uint16 | Read | 0xB800..0xB820
47105 | 2 |  | 4 | Temperature Node18 | oC |  | float | Read
47107 | 1 |  | 2 | Status Node 18 | 0-255 |  | uint16 | Read
47360 | 1 |  | 2 | %Battery Node19 | 10,30,60,99 |  | uint16 | Read | 0xB900..0xB920
47361 | 2 |  | 4 | Temperature Node19 | oC |  | float | Read
47363 | 1 |  | 2 | Status Node 19 | 0-255 |  | uint16 | Read
47616 | 1 |  | 2 | %Battery Node20 | 10,30,60,99 |  | uint16 | Read | 0xBA00..0xBA20
47617 | 2 |  | 4 | Temperature Node20 | oC |  | float | Read
47619 | 1 |  | 2 | Status Node 20 | 0-255 |  | uint16 | Read
49408 | 1 |  | 2 | %Battery Node21 | 10,30,60,99 |  | uint16 | Read | 0xC100..0xC120
49409 | 2 |  | 4 | Temperature Node21 | oC |  | float | Read
49411 | 1 |  | 2 | Status Node 21 | 0-255 |  | uint16 | Read
49664 | 1 |  | 2 | %Battery Node22 | 10,30,60,99 |  | uint16 | Read | 0xC200..0xC220
49665 | 2 |  | 4 | Temperature Node22 | oC |  | float | Read
49667 | 1 |  | 2 | Status Node 22 | 0-255 |  | uint16 | Read
49920 | 1 |  | 2 | %Battery Node23 | 10,30,60,99 |  | uint16 | Read | 0xC300..0xC320
49921 | 2 |  | 4 | Temperature Node23 | oC |  | float | Read
49923 | 1 |  | 2 | Status Node 23 | 0-255 |  | uint16 | Read
50176 | 1 |  | 2 | %Battery Node24 | 10,30,60,99 |  | uint16 | Read | 0xC400..0xC420
50177 | 2 |  | 4 | Temperature Node24 | oC |  | float | Read
50179 | 1 |  | 2 | Status Node 24 | 0-255 |  | uint16 | Read
50432 | 1 |  | 2 | %Battery Node25 | 10,30,60,99 |  | uint16 | Read | 0xC500..0xC520
50433 | 2 |  | 4 | Temperature Node25 | oC |  | float | Read
50435 | 1 |  | 2 | Status Node 25 | 0-255 |  | uint16 | Read
50688 | 1 |  | 2 | %Battery Node26 | 10,30,60,99 |  | uint16 | Read | 0xC600..0xC620
50689 | 2 |  | 4 | Temperature Node26 | oC |  | float | Read
50691 | 1 |  | 2 | Status Node 26 | 0-255 |  | uint16 | Read
50944 | 1 |  | 2 | %Battery Node27 | 10,30,60,99 |  | uint16 | Read | 0xC700..0xC720
50945 | 2 |  | 4 | Temperature Node27 | oC |  | float | Read
50947 | 1 |  | 2 | Status Node 27 | 0-255 |  | uint16 | Read
51200 | 1 |  | 2 | %Battery Node28 | 10,30,60,99 |  | uint16 | Read | 0xC800..0xC820
51201 | 2 |  | 4 | Temperature Node28 | oC |  | float | Read
51203 | 1 |  | 2 | Status Node 28 | 0-255 |  | uint16 | Read
51456 | 1 |  | 2 | %Battery Node29 | 10,30,60,99 |  | uint16 | Read | 0xC900..0xC920
51457 | 2 |  | 4 | Temperature Node29 | oC |  | float | Read
51459 | 1 |  | 2 | Status Node 29 | 0-255 |  | uint16 | Read
51712 | 1 |  | 2 | %Battery Node30 | 10,30,60,99 |  | uint16 | Read | 0xCA00..0xCA20
51713 | 2 |  | 4 | Temperature Node30 | oC |  | float | Read
51715 | 1 |  | 2 | Status Node 30 | 0-255 |  | uint16 | Read
53504 | 1 |  | 2 | %Battery Node31 | 10,30,60,99 |  | uint16 | Read | 0xD100..0xD120
53505 | 2 |  | 4 | Temperature Node31 | oC |  | float | Read
53507 | 1 |  | 2 | Status Node 31 | 0-255 |  | uint16 | Read
53760 | 1 |  | 2 | %Battery Node32 | 10,30,60,99 |  | uint16 | Read | 0xD200..0xD220
53761 | 2 |  | 4 | Temperature Node32 | oC |  | float | Read
53763 | 1 |  | 2 | Status Node 32 | 0-255 |  | uint16 | Read
54016 | 1 |  | 2 | %Battery Node33 | 10,30,60,99 |  | uint16 | Read | 0xD300..0xD320
54017 | 2 |  | 4 | Temperature Node33 | oC |  | float | Read
54019 | 1 |  | 2 | Status Node 33 | 0-255 |  | uint16 | Read
54272 | 1 |  | 2 | %Battery Node34 | 10,30,60,99 |  | uint16 | Read | 0xD400..0xD420
54273 | 2 |  | 4 | Temperature Node34 | oC |  | float | Read
54275 | 1 |  | 2 | Status Node 34 | 0-255 |  | uint16 | Read
54528 | 1 |  | 2 | %Battery Node35 | 10,30,60,99 |  | uint16 | Read | 0xD500..0xD520
54529 | 2 |  | 4 | Temperature Node35 | oC |  | float | Read
54531 | 1 |  | 2 | Status Node 35 | 0-255 |  | uint16 | Read
54784 | 1 |  | 2 | %Battery Node36 | 10,30,60,99 |  | uint16 | Read | 0xD600..0xD620
54785 | 2 |  | 4 | Temperature Node36 | oC |  | float | Read
54787 | 1 |  | 2 | Status Node 36 | 0-255 |  | uint16 | Read
55040 | 1 |  | 2 | %Battery Node37 | 10,30,60,99 |  | uint16 | Read | 0xD700..0xD720
55041 | 2 |  | 4 | Temperature Node37 | oC |  | float | Read
55043 | 1 |  | 2 | Status Node 37 | 0-255 |  | uint16 | Read
55296 | 1 |  | 2 | %Battery Node38 | 10,30,60,99 |  | uint16 | Read | 0xD800..0xD820
55297 | 2 |  | 4 | Temperature Node38 | oC |  | float | Read
55299 | 1 |  | 2 | Status Node 38 | 0-255 |  | uint16 | Read
55552 | 1 |  | 2 | %Battery Node39 | 10,30,60,99 |  | uint16 | Read | 0xD900..0xD920
55553 | 2 |  | 4 | Temperature Node39 | oC |  | float | Read
55555 | 1 |  | 2 | Status Node 39 | 0-255 |  | uint16 | Read
55808 | 1 |  | 2 | %Battery Node40 | 10,30,60,99 |  | uint16 | Read | 0xDA00..0xDA20
55809 | 2 |  | 4 | Temperature Node40 | oC |  | float | Read
55811 | 1 |  | 2 | Status Node 40 | 0-255 |  | uint16 | Read

## Data area of sensor là Press.
Modbus Register | # of register | Adr | Size | Description | Range | Default | Format | Property | Comment
41216 | 1 |  | 2 | %Battery Node1 | 10,30,60,99 |  | uint16 | Read | Wireless Sensor là loại cảm biến áp suất, 0xA100..0xA120
41217 | 2 |  | 4 | Pressure Node1 | % |  | float | Read | Pressure output = 0%..100%
41219 | 1 |  | 2 | Status Node1 | 0-255 |  | uint16 | Read | Ý nghĩa status của sensor 1: + Status = 0: không có cảm biến or cảm biến hư + Status = 1: cảm biến nhiệt độ + Status = 2: cảm biến độ ẩm + Status = 3: cảm biến chênh áp môi trường + Status = 4: cảm biến áp suất … Status = n: cảm biến + Status = 255: đã thay đổi loại cảm biến mà chưa reset để nhận dạng cảm biến mới + Status = 254: sensor port chạm GND + Status = 253: sensor port chạm Vcc + Status = 252: sensor port chạm nhau
41220 | 2 |  | 4 | Temperature Node1 | oC |  | float | Read
41472 | 1 |  | 2 | %Battery Node2 | 10,30,60,99 |  | uint16 | Read | 0xA200..0xA220
41473 | 2 |  | 4 | Pressure Node2 | % |  | float | Read
41475 | 1 |  | 2 | Status Node2 | 0-255 |  | uint16 | Read
41476 | 2 |  | 4 | Temperature Node2 | oC |  | float | Read
41728 | 1 |  | 2 | %Battery Node3 | 10,30,60,99 |  | uint16 | Read | 0xA300..0xA320
41729 | 2 |  | 4 | Pressure Node3 | % |  | float | Read
41731 | 1 |  | 2 | Status Node3 | 0-255 |  | uint16 | Read
41732 | 2 |  | 4 | Temperature Node3 | oC |  | float | Read
41984 | 1 |  | 2 | %Battery Node4 | 10,30,60,99 |  | uint16 | Read | 0xA400..0xA420
41985 | 2 |  | 4 | Pressure Node4 | % |  | float | Read
41987 | 1 |  | 2 | Status Node4 | 0-255 |  | uint16 | Read
41988 | 2 |  | 4 | Temperature Node4 | oC |  | float | Read
42240 | 1 |  | 2 | %Battery Node5 | 10,30,60,99 |  | uint16 | Read | 0xA500..0xA520
42241 | 2 |  | 4 | Pressure Node5 | % |  | float | Read
42243 | 1 |  | 2 | Status Node5 | 0-255 |  | uint16 | Read
42244 | 2 |  | 4 | Temperature Node5 | oC |  | float | Read
42496 | 1 |  | 2 | %Battery Node6 | 10,30,60,99 |  | uint16 | Read | 0xA600..0xA620
42497 | 2 |  | 4 | Pressure Node6 | % |  | float | Read
42499 | 1 |  | 2 | Status Node6 | 0-255 |  | uint16 | Read
42500 | 2 |  | 4 | Temperature Node6 | oC |  | float | Read
42752 | 1 |  | 2 | %Battery Node7 | 10,30,60,99 |  | uint16 | Read | 0xA700..0xA720
42753 | 2 |  | 4 | Pressure Node7 | % |  | float | Read
42755 | 1 |  | 2 | Status Node7 | 0-255 |  | uint16 | Read
42756 | 2 |  | 4 | Temperature Node7 | oC |  | float | Read
43008 | 1 |  | 2 | %Battery Node8 | 10,30,60,99 |  | uint16 | Read | 0xA800..0xA820
43009 | 2 |  | 4 | Pressure Node8 | % |  | float | Read
43011 | 1 |  | 2 | Status Node8 | 0-255 |  | uint16 | Read
43012 | 2 |  | 4 | Temperature Node8 | oC |  | float | Read
43264 | 1 |  | 2 | %Battery Node9 | 10,30,60,99 |  | uint16 | Read | 0xA900..0xA920
43265 | 2 |  | 4 | Pressure Node9 | % |  | float | Read
43267 | 1 |  | 2 | Status Node9 | 0-255 |  | uint16 | Read
43268 | 2 |  | 4 | Temperature Node9 | oC |  | float | Read
43520 | 1 |  | 2 | %Battery Node10 | 10,30,60,99 |  | uint16 | Read | 0xAA00..0xAA20
43521 | 2 |  | 4 | Pressure Node10 | % |  | float | Read
43523 | 1 |  | 2 | Status Node10 | 0-255 |  | uint16 | Read
43524 | 2 |  | 4 | Temperature Node10 | oC |  | float | Read
45312 | 1 |  | 2 | %Battery Node11 | 10,30,60,99 |  | uint16 | Read | 0xB100..0xB120
45313 | 2 |  | 4 | Pressure Node11 | % |  | float | Read
45315 | 1 |  | 2 | Status Node11 | 0-255 |  | uint16 | Read
45316 | 2 |  | 4 | Temperature Node11 | oC |  | float | Read
45568 | 1 |  | 2 | %Battery Node12 | 10,30,60,99 |  | uint16 | Read | 0xB200..0xB220
45569 | 2 |  | 4 | Pressure Node12 | % |  | float | Read
45571 | 1 |  | 2 | Status Node12 | 0-255 |  | uint16 | Read
45572 | 2 |  | 4 | Temperature Node12 | oC |  | float | Read
45824 | 1 |  | 2 | %Battery Node13 | 10,30,60,99 |  | uint16 | Read | 0xB300..0xB320
45825 | 2 |  | 4 | Pressure Node13 | % |  | float | Read
45827 | 1 |  | 2 | Status Node13 | 0-255 |  | uint16 | Read
45828 | 2 |  | 4 | Temperature Node13 | oC |  | float | Read
46080 | 1 |  | 2 | %Battery Node14 | 10,30,60,99 |  | uint16 | Read | 0xB400..0xB420
46081 | 2 |  | 4 | Pressure Node14 | % |  | float | Read
46083 | 1 |  | 2 | Status Node14 | 0-255 |  | uint16 | Read
46084 | 2 |  | 4 | Temperature Node14 | oC |  | float | Read
46336 | 1 |  | 2 | %Battery Node15 | 10,30,60,99 |  | uint16 | Read | 0xB500..0xB520
46337 | 2 |  | 4 | Pressure Node15 | % |  | float | Read
46339 | 1 |  | 2 | Status Node15 | 0-255 |  | uint16 | Read
46340 | 2 |  | 4 | Temperature Node15 | oC |  | float | Read
46592 | 1 |  | 2 | %Battery Node16 | 10,30,60,99 |  | uint16 | Read | 0xB600..0xB620
46593 | 2 |  | 4 | Pressure Node16 | % |  | float | Read
46595 | 1 |  | 2 | Status Node16 | 0-255 |  | uint16 | Read
46596 | 2 |  | 4 | Temperature Node16 | oC |  | float | Read
46848 | 1 |  | 2 | %Battery Node17 | 10,30,60,99 |  | uint16 | Read | 0xB700..0xB720
46849 | 2 |  | 4 | Pressure Node17 | % |  | float | Read
46851 | 1 |  | 2 | Status Node17 | 0-255 |  | uint16 | Read
46852 | 2 |  | 4 | Temperature Node17 | oC |  | float | Read
47104 | 1 |  | 2 | %Battery Node18 | 10,30,60,99 |  | uint16 | Read | 0xB800..0xB820
47105 | 2 |  | 4 | Pressure Node18 | % |  | float | Read
47107 | 1 |  | 2 | Status Node18 | 0-255 |  | uint16 | Read
47108 | 2 |  | 4 | Temperature Node18 | oC |  | float | Read
47360 | 1 |  | 2 | %Battery Node19 | 10,30,60,99 |  | uint16 | Read | 0xB900..0xB920
47361 | 2 |  | 4 | Pressure Node19 | % |  | float | Read
47363 | 1 |  | 2 | Status Node19 | 0-255 |  | uint16 | Read
47364 | 2 |  | 4 | Temperature Node19 | oC |  | float | Read
47616 | 1 |  | 2 | %Battery Node20 | 10,30,60,99 |  | uint16 | Read | 0xBA00..0xBA20
47617 | 2 |  | 4 | Pressure Node20 | % |  | float | Read
47619 | 1 |  | 2 | Status Node20 | 0-255 |  | uint16 | Read
47620 | 2 |  | 4 | Temperature Node20 | oC |  | float | Read
49408 | 1 |  | 2 | %Battery Node21 | 10,30,60,99 |  | uint16 | Read | 0xC100..0xC120
49409 | 2 |  | 4 | Pressure Node21 | % |  | float | Read
49411 | 1 |  | 2 | Status Node21 | 0-255 |  | uint16 | Read
49412 | 2 |  | 4 | Temperature Node21 | oC |  | float | Read
49664 | 1 |  | 2 | %Battery Node22 | 10,30,60,99 |  | uint16 | Read | 0xC200..0xC220
49665 | 2 |  | 4 | Pressure Node22 | % |  | float | Read
49667 | 1 |  | 2 | Status Node22 | 0-255 |  | uint16 | Read
49668 | 2 |  | 4 | Temperature Node22 | oC |  | float | Read
49920 | 1 |  | 2 | %Battery Node23 | 10,30,60,99 |  | uint16 | Read | 0xC300..0xC320
49921 | 2 |  | 4 | Pressure Node23 | % |  | float | Read
49923 | 1 |  | 2 | Status Node23 | 0-255 |  | uint16 | Read
49924 | 2 |  | 4 | Temperature Node23 | oC |  | float | Read
50176 | 1 |  | 2 | %Battery Node24 | 10,30,60,99 |  | uint16 | Read | 0xC400..0xC420
50177 | 2 |  | 4 | Pressure Node24 | % |  | float | Read
50179 | 1 |  | 2 | Status Node24 | 0-255 |  | uint16 | Read
50180 | 2 |  | 4 | Temperature Node24 | oC |  | float | Read
50432 | 1 |  | 2 | %Battery Node25 | 10,30,60,99 |  | uint16 | Read | 0xC500..0xC520
50433 | 2 |  | 4 | Pressure Node25 | % |  | float | Read
50435 | 1 |  | 2 | Status Node25 | 0-255 |  | uint16 | Read
50436 | 2 |  | 4 | Temperature Node25 | oC |  | float | Read
50688 | 1 |  | 2 | %Battery Node26 | 10,30,60,99 |  | uint16 | Read | 0xC600..0xC620
50689 | 2 |  | 4 | Pressure Node26 | % |  | float | Read
50691 | 1 |  | 2 | Status Node26 | 0-255 |  | uint16 | Read
50692 | 2 |  | 4 | Temperature Node26 | oC |  | float | Read
50944 | 1 |  | 2 | %Battery Node27 | 10,30,60,99 |  | uint16 | Read | 0xC700..0xC720
50945 | 2 |  | 4 | Pressure Node27 | % |  | float | Read
50947 | 1 |  | 2 | Status Node27 | 0-255 |  | uint16 | Read
50948 | 2 |  | 4 | Temperature Node27 | oC |  | float | Read
51200 | 1 |  | 2 | %Battery Node28 | 10,30,60,99 |  | uint16 | Read | 0xC800..0xC820
51201 | 2 |  | 4 | Pressure Node28 | % |  | float | Read
51203 | 1 |  | 2 | Status Node28 | 0-255 |  | uint16 | Read
51204 | 2 |  | 4 | Temperature Node28 | oC |  | float | Read
51456 | 1 |  | 2 | %Battery Node29 | 10,30,60,99 |  | uint16 | Read | 0xC900..0xC920
51457 | 2 |  | 4 | Pressure Node29 | % |  | float | Read
51459 | 1 |  | 2 | Status Node29 | 0-255 |  | uint16 | Read
51460 | 2 |  | 4 | Temperature Node29 | oC |  | float | Read
51712 | 1 |  | 2 | %Battery Node30 | 10,30,60,99 |  | uint16 | Read | 0xCA00..0xCA20
51713 | 2 |  | 4 | Pressure Node30 | % |  | float | Read
51715 | 1 |  | 2 | Status Node30 | 0-255 |  | uint16 | Read
51716 | 2 |  | 4 | Temperature Node30 | oC |  | float | Read
53504 | 1 |  | 2 | %Battery Node31 | 10,30,60,99 |  | uint16 | Read | 0xD100..0xD120
53505 | 2 |  | 4 | Pressure Node31 | % |  | float | Read
53507 | 1 |  | 2 | Status Node31 | 0-255 |  | uint16 | Read
53508 | 2 |  | 4 | Temperature Node31 | oC |  | float | Read
53760 | 1 |  | 2 | %Battery Node32 | 10,30,60,99 |  | uint16 | Read | 0xD200..0xD220
53761 | 2 |  | 4 | Pressure Node32 | % |  | float | Read
53763 | 1 |  | 2 | Status Node32 | 0-255 |  | uint16 | Read
53764 | 2 |  | 4 | Temperature Node32 | oC |  | float | Read
54016 | 1 |  | 2 | %Battery Node33 | 10,30,60,99 |  | uint16 | Read | 0xD300..0xD320
54017 | 2 |  | 4 | Pressure Node33 | % |  | float | Read
54019 | 1 |  | 2 | Status Node33 | 0-255 |  | uint16 | Read
54020 | 2 |  | 4 | Temperature Node33 | oC |  | float | Read
54272 | 1 |  | 2 | %Battery Node34 | 10,30,60,99 |  | uint16 | Read | 0xD400..0xD420
54273 | 2 |  | 4 | Pressure Node34 | % |  | float | Read
54275 | 1 |  | 2 | Status Node34 | 0-255 |  | uint16 | Read
54276 | 2 |  | 4 | Temperature Node34 | oC |  | float | Read
54528 | 1 |  | 2 | %Battery Node35 | 10,30,60,99 |  | uint16 | Read | 0xD500..0xD520
54529 | 2 |  | 4 | Pressure Node35 | % |  | float | Read
54531 | 1 |  | 2 | Status Node35 | 0-255 |  | uint16 | Read
54532 | 2 |  | 4 | Temperature Node35 | oC |  | float | Read
54784 | 1 |  | 2 | %Battery Node36 | 10,30,60,99 |  | uint16 | Read | 0xD600..0xD620
54785 | 2 |  | 4 | Pressure Node36 | % |  | float | Read
54787 | 1 |  | 2 | Status Node36 | 0-255 |  | uint16 | Read
54788 | 2 |  | 4 | Temperature Node36 | oC |  | float | Read
55040 | 1 |  | 2 | %Battery Node37 | 10,30,60,99 |  | uint16 | Read | 0xD700..0xD720
55041 | 2 |  | 4 | Pressure Node37 | % |  | float | Read
55043 | 1 |  | 2 | Status Node37 | 0-255 |  | uint16 | Read
55044 | 2 |  | 4 | Temperature Node37 | oC |  | float | Read
55296 | 1 |  | 2 | %Battery Node38 | 10,30,60,99 |  | uint16 | Read | 0xD800..0xD820
55297 | 2 |  | 4 | Pressure Node38 | % |  | float | Read
55299 | 1 |  | 2 | Status Node38 | 0-255 |  | uint16 | Read
55300 | 2 |  | 4 | Temperature Node38 | oC |  | float | Read
55552 | 1 |  | 2 | %Battery Node39 | 10,30,60,99 |  | uint16 | Read | 0xD900..0xD920
55553 | 2 |  | 4 | Pressure Node39 | % |  | float | Read
55555 | 1 |  | 2 | Status Node39 | 0-255 |  | uint16 | Read
55556 | 2 |  | 4 | Temperature Node39 | oC |  | float | Read
55808 | 1 |  | 2 | %Battery Node40 | 10,30,60,99 |  | uint16 | Read | 0xDA00..0xDA20
55809 | 2 |  | 4 | Pressure Node40 | % |  | float | Read
55811 | 1 |  | 2 | Status Node40 | 0-255 |  | uint16 | Read
55812 | 2 |  | 4 | Temperature Node40 | oC |  | float | Read